## Prj Legend
MTEP Database Export
Project Table Field Legend
Appendix A contains projects which are being or have been approved by MISO Board of Directors.
Transmission Owners are obligated to make a good faith effort to construct projects in Appendix A.
Appendix B projects have been reviewed by MISO staff for need and effectivenes.
Project table has blue highlighted header. A project may have multiple facilties.
Facility table has beige highlighted header. A project's facilities may have different in service dates.
Project Table Field Legend
Field | Description
Target Appendix | Target appendix for the MTEPyy planning cycle. Example: "A in MTEP15" projects were reviewed in MTEP15. .
Region | MISO Planning Region: Central, East, West or South
Geographic Location by TO Member System | Project geographic location by Transmission Owner member systems
PrjID | Project ID: MISO project identifier
Project Name | Project name (short name)
Project Description | A description of the project's components
State 1 | State project is located or first state if in multiple states
State 2 | If applicable, the second state the project is located
Allocation Type per FF | Project Type per Attachment FF of Tariff. BaseRel is Baseline Reliability, GIP is Generator Interconnection Project, TDSP is Transmission Delivery Service Project, MEP is Market Efficiency Project, MVP is Multi Value Project, Other is none of the above. Preliminary project allocation types may be designated for projects in Appendix B
Share Status | Cost allocation status for projects in Appendix A or moving to Appendix A in current planning cycle. Projects are Shared, Not Shared or Excluded. Preliminary sharing designations may be input for Appendix B projects
Other Type | Indicates the project driver behind Other type projects.
Estimated Cost | Total estimated project cost from Facility table
Expected ISD (Min/Max) | Dates when project is expected to be in service. Min and Max dates. Expected ISD are in Facility table.
Max kV | Maximum facility voltage in project. Summary information from Facility table
Min kV | Minimum facility voltage in project. Summary information form Facility table

## Projects
Target Appendix | Planning Region | Geographic Location by TO Member System | PrjId | Project Name | Project Description | State1 | State2 | Need Date | System Need | Alternatives | Withdrawal Reason | Comments | Submitting Comp. | Allocation Type per FF | Share Status | Other Type | Expected ISD (Min) | Expected ISD (Max) | Max kV | Min kV | Min of Plan Status | Estimated Cost
A in MTEP21 | South | AECC | 20161 | Tap EAL Monticello East - Reed: Construct Selma South 115/69 kV substation | Tap Entergy's Monticello to Reed 115 kV transmission and construct the Selma South 115/69 kV, 60/80/100 MVA transmission substation. | AR | AR | 2024-04-01 | This delivery point is needed to improve reliability to the C&L Electric Cooperative 69 kV transmission system currently served by the Glendale delivery point. |  |  | Selma South will served a portion of the load currently served by Glendale. However, for the loss of Glendale, Selma South will serve 100% of the load currently served by Glendale. | Arkansas Electric Coopertive Corporation | Other |  | Reliability | 2024-01-01 | 2024-01-01 | 115 | 0 | Proposed | 7500000
A in MTEP21 | South | AECC | 20265 | Glendale Capacitor Bank | Install 9.6 MVAR capacitor bank at Glendale. | AR | AR | 2024-05-01 | This project is needed in conjunction with the Selma South transmission substation. For the loss of the Glendale delivery point, Selma South needs additional voltage support from a capacitor bank to serve the C&L 69 kV transmission system. |  |  | Glendale is an existing delivery point that serves C&L's 69 kV transmission system. | Arkansas Electric Coopertive Corporation | Other |  | Reliability | 2024-01-01 | 2024-01-01 | 69 | 0 | Proposed | 1000000
A in MTEP21 | West | ATC | 10590 | Academy - Columbus, 69kV (Y-21), rebuild & OPGW | The Academy - Columbus (Y-21) 69kV circuit is 3 miles long and uses 336 kcmil ACSR supported on lattice steel structures - Field inspection reports indicate the 1910 vintage structures require replacement to continue reliable operation - New conductor will be installed and will be similar or slightly larger than the existing circuit capability - Optical Ground Wire (OPGW) will be installed to provide protection and SCADA communications along this ROW Substation Work Scope: - Academy Substation - Replace line side jumper to meet planning long term rating needs and terminate fiber. - Columbus (ALTE) - Remove control house, oil circuit breakers, and switches; - Install motor operated disconnects, gas circuit breaker, control house, and RTU for SCADA control - Improve drive access to site with purchase and demolition of existing residence - Terminate fiber with line project. | WI | WI | 2024-12-31 | Asset Renewal - Line Rebuild |  |  |  | American Transmission Co. LLC | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 0 | Proposed | 8800000
A in MTEP21 | West | ATC | 14964 | Small Capital Project and Asset Renewal Program 2022 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, re-insulations and uprates and Pole hardware replacements - Estimated Cost - $4,000,000 Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. - Estimated Cost - $40,000,000 Substation Battery Replacement Program - Estimated Cost - $3,000,000 Substation Physical Security Asset Renewal - Estimated Cost - $3,000,000 Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | WI,MI | WI,MI | 2025-06-30 | Asset Renewal or Reliability |  |  |  | American Transmission Co. LLC | Other |  | Age and Condition | 2025-06-30 | 2025-06-30 | 345 | 69 | Proposed | 52320773
A in MTEP21 | West | ATC | 14965 | Communication Reliability Program 2022 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | WI,MI | WI,MI | 2025-06-30 | Communications |  |  |  | American Transmission Co. LLC | Other |  | Other Local Needs | 2025-06-30 | 2025-06-30 | 345 | 69 | Proposed | 19252066
A in MTEP21 | West | ATC | 14966 | Line Clearance Mitigation Program 2022 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2022. | WI,MI | WI,MI | 2025-06-30 | Line Clearance |  |  |  | American Transmission Co. LLC | Other |  | Reliability | 2025-06-30 | 2025-06-30 | 345 | 69 | Proposed | 2832841
A in MTEP21 | West | ATC | 14967 | Physical Security Program 2022 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2022. | WI,MI | WI,MI | 2025-06-30 | Physical Security |  |  |  | American Transmission Co. LLC | Other |  | Other Local Needs | 2025-06-30 | 2025-06-30 | 345 | 69 | Proposed | 11797871
A in MTEP21 | West | ATC | 14968 | Load Interconnection Program 2022 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | WI,MI | WI,MI | 2025-06-30 | Load Interconnection |  |  |  | American Transmission Co. LLC | Other |  | Load Growth | 2025-06-30 | 2025-06-30 | 138 | 69 | Proposed | 27586994
A in MTEP21 | West | ATC | 16489 | Empire SS, Control House, Relays, and Circuit Breaker Asset Renewal | Asset renewal at the Empire SS would include: - Install new control building - Retirement and replacement of circuit breakers, protective relays, and disconnect switches | MI | MI | 2024-12-31 | Asset Renewal - Substation |  |  |  | American Transmission Co. LLC | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 138 | 138 | Proposed | 9900000
A in MTEP21 | West | ATC | 16490 | Granville SS, Control House and Relay Replacement and Asset Renewal | 345kV Project Scope • Replace 4 1970-vintage Westinghouse 3450-GW-25000 oil breakers • Replace 7 disconnect switches 138kV Project Scope • Replace 7 1969-vintage Westinghouse 1380-GM-15000 oil breakers • Replace 2 underground HPFF lines with overhead and retire pump house at Granville and East Granville Terminal General Project Scope • Reconfigure 345kV bus to 6-position ring (5 positions plus one future position) • Vacate existing control house, transfer ownership to We Energies, obtain new high-security control house • Replace all relays and SCADA with current standard • Address planning-identified need for redundant bus differential protection • Expand yard to accommodate ring bus | WI | WI | 2024-12-01 | Asset Renewal - Substation |  |  |  | American Transmission Co. LLC | Other |  | Age and Condition | 2024-12-01 | 2024-12-01 | 345 | 138 | Proposed | 28950000
A in MTEP21 | West | ATC | 18048 | Lincoln - 43rd Street Terminal 138 kV (5053), Replace with double circuit duct bank and XLPE cable | • Rebuild existing 5053 HPFF line with new XLPE in double circuit duct bank in existing road ROW. o Install ~2.2 miles of XLPE in double circuit duct bank package and new manholes. | WI | WI | 2024-12-31 | Asset Renewal - Line Rebuild |  |  |  | American Transmission Co. LLC | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 35800000
A in MTEP21 | West | ATC | 19105 | Nelson Dewey SS - Control House, Relay Asset Renewal | • Replace control house and contents, including but not limited to: - Relays and panels, relocating and reusing five reply panels in the new house - Two batteries and charger - Project team will evaluate location and elevation and relay panel design to mitigate flood risk • Replace control cabling between new control house and all station equipment | WI | WI | 2024-12-31 | Asset Renewal - Substation |  |  |  | American Transmission Co. LLC | Other |  | Age and Condition | 2022-06-01 | 2022-06-01 | 138 | 69 | Proposed | 6170000
A in MTEP21 | West | ATC | 19587 | Petenwell – Council Creek, (X-40) 138kV, Partial Structure and OPGW Replacement | - Replace 30 miles of shield wire with 48 Strand OPGW Fiber cable between Petenwell and Council Creek substations - Replace ~67 wood monopoles structures | WI | WI | 2024-12-31 | Communications |  |  |  | American Transmission Co. LLC | Other |  | Other Local Needs | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 9000000
A in MTEP21 | West | ATC | 19705 | Crivitz SS, Transformers and Relays Asset Renewal | • Replace T1, 138/69 kV power transformer with the on-site 138/69 kV system spare • Replace T3, 138/69 kV power transformer with the 138/69kV power transformer from Pioneer SS that will be taken out of service in 2023 due to elimination of the 69 kV system at that substation • Replace 69 kV Mark V circuit switcher with an existing on site circuit breaker and new disconnect switch • Replace a single line relay in an existing panel | WI | WI | 2024-12-31 | Asset Renewal - Substation |  |  |  | American Transmission Co. LLC | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 4599154
A in MTEP21 | West | ATC | 19706 | North Appleton SS, Transformer and Reactor Asset Renewal | • Replace T7 138/345 kV power transformer (three single phase units) with the on-site system spare (standard three phase). • Retire two three-phase reactors, bus, structures and insulators and install a new standard 24.9 kV design connected to the tertiary of the newly installed 138/345 kV power transformer • Retire original design 34.5 kV vacuum breaker and associated disconnect switches • Install new station service on 24.9 kV bus salvaging three newer vintage reactors for use in a future project • Replace seven 138 kV disconnect switches | WI | WI | 2024-12-01 | Asset Renewal - Substation |  |  |  | American Transmission Co. LLC | Other |  | Age and Condition | 2024-12-01 | 2024-12-01 | 345 | 0 | Proposed | 7938249
A in MTEP21 | West | ATC | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | Interconnection of about 560 MW the facility composed of one (1) steam turbine unit and one (1) natural gas unit in a 1x1 combined cycle facility interconnecting at the new Superior Substation. | WI | WI | 2023-11-30 | Inteconnection |  |  |  | American Transmission Co. LLC | GIP | Shared |  | 2023-11-30 | 2023-11-30 | 345 | 230 | Proposed | 21245605
A in MTEP21 | West | ATC | 19806 | Bonnie Road SS, DIC, New Substation | • Extend approximately 0.38 miles of 69 kV double circuit transmission line on new right-of-way. • Construct new 69 kV substation with a bus-tie switch and provisions for a future bus-tie breaker. • Install 69 kV line breakers as sectionalizing devices. | WI | WI | 2023-06-01 | Load Interconnection |  |  |  | American Transmission Co. LLC | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 69 | 0 | Proposed | 3504413
A in MTEP21 | West | ATC | 19959 | Sussex to Bark River (46143/2661), 138kV, OPGW Installation | Install 8 miles of fiber optic cable between the Sussex to Bark River substations and terminate it within the control houses. | WI | WI | 2023-12-31 | Communications |  |  |  | American Transmission Co. LLC | Other |  | Other Local Needs | 2023-12-31 | 2023-12-31 | 138 | 0 | Proposed | 3766000
A in MTEP21 | West | ATC | 19961 | Wells St. DIC – New West Marinette-Wells St. 69 kV line | -Construct a new 69kV transmission line from West Marinette SS to Wells St. SS -Rebuild the existing 1.6 mile portion of the West Marinette-Roosevelt Rd. 69 kV as double-circuit -Add a 2nd 69 kV circuit on the existing overhead 1.9 mile section of Roosevelt Rd.-Wells St. -Add a 2nd underground cable in the spare conduit ducts from Riser Structure #27 to Wells St. -At the West Marinette SS add a new 69kV bus position and circuit breaker | WI | WI | 2024-05-31 | Load Interconnection |  |  |  | American Transmission Co. LLC | Other |  | Load Growth | 2024-05-31 | 2024-05-31 | 69 | 0 | Proposed | 16100000
A in MTEP21 | West | ATC | 19965 | Marquette County Reactive Power Project | Relocate one 138 kV line position (line 16343) to a different bus position at National substation. • Install one +/- 50 MVA, 138 kV STATCOM (Static Synchronous Compensator) at National substation. o Include one spare 138 kV transformer o Add a new 138 kV circuit breaker and protection package at National | MI | MI | 2023-12-01 | Reliability The central U.P. experiences voltage limitations on a regular basis due to the retirement of the Presque Isle Power Plant generation and the consistent off-line operation of the RICE units at Mihm and Kuester each night. • High intact system voltages • Single-contingency low voltage limitations • Limited reactive power control in this area |  |  |  | American Transmission Co. LLC | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 138 | 0 | Proposed | 24200000
A in MTEP21 | West | ATC | 20625 | J986 7 Mile Creek SS, Generator Interconnection Facilities and Network Upgrades | J986 is a proposed 149.76 MW solar farm power plant in Wood County, Wisconsin. | WI | WI | 2022-06-01 | Interconnection |  |  |  | American Transmission Co. LLC | GIP |  |  | 2022-06-01 | 2022-06-01 | 138 | 69 | Proposed | 17564028
A in MTEP21 | West | ATC | 20785 | Highway V -Preble 138 kV (X-154), reconductor | The Highway V-Preble 138 kV line reconductor project consists of the following: -Reconductor 138kV line from Highway V to Preble -Replace five 138 kV jumpers at Highway V -Replace one 138 kV jumper at Preble | WI | WI | 2023-05-15 | Reliability |  |  |  | American Transmission Co. LLC | BRP |  |  | 2023-05-15 | 2023-05-15 | 138 | 0 | Proposed | 1777603
A in MTEP21 | West | ATC | 20925 | Lancaster Transformer Replacement & Substation Rebuild | ATC will retire the Lancaster 138/69 kV transformer, 69 kV bus, and associated equipment and expand the 138 kV bus (box structure) and add bus-tie switches and space provisions for a future bus-tie breaker. In addition: - install 2 circuit breakers on line X-1 - replace the control house and relay equipment | WI | WI | 2023-12-31 | Load Interconnection |  |  |  | American Transmission Co. LLC | Other |  | Load Growth | 2023-12-31 | 2023-12-31 | 138 | 69 | Proposed | 3700000
A in MTEP21 | Central | AmerenIL | 9843 | New Normal East 138/34.5 kV transformer | Install 112 MVA Transformer | IL | IL | 2017-05-26 | Local load serving need |  |  | Project complete 05/26/2017. Project moved to Target A for MTEP16 after Board Approval in 2017 so it was not formally approved. It will be presented in MTEP21. | Ameren Services Company | Other | Not Shared | Load Growth | 2017-05-26 | 2017-05-26 | 138 | 34.5 | In Service | 1500000
A in MTEP21 | Central | AmerenIL | 16989 | New Mattoon W 138 kV substation | Install new 6 position ultimate ring bus at Mattoon West Substation. | IL | IL | 2023-12-01 | Increased reliability and operating flexibility. |  |  |  | Ameren Services Company | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 138 | 0 | Planned | 8500000
A in MTEP21 | Central | AmerenIL | 16990 | New Kline 138 kV substation | Install new 6 position ultimate ring bus at Kline Substation (formerly known as Wanda). | IL | IL | 2022-06-01 | This project will increase reliability and flexibility of the transmission system and to the customers supplied from the existing substation. A fault on the bus or transformer would outage the entire substation. The new substation will also accommodate future transmission expansion. |  |  |  | Ameren Services Company | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 138 | 0 | Planned | 7200000
A in MTEP21 | Central | AmerenIL | 17864 | Upgrade Cahokia 345/138 kV substation | Replace OCB H27 on the C-GRAT-3 position and OCB H35 on the C-RUSL-2 positon with symmetrically rated SF6 55 kA circuit breakers. | IL | IL | 2022-12-01 | General system expansion has increased the fault duty on these breakers, necessitating their replacement. |  |  |  | Ameren Services Company | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 138 | 0 | Planned | 4200000
A in MTEP21 | Central | AmerenIL | 17979 | Rebuild North Staunton 138 kV substation | Rebuild the North Staunton 138 kV substation to a ring bus configuration. New name is Rezzy. | IL | IL | 2022-12-01 | This project will increase reliability and flexibility of the transmission system and to the customers supplied from the existing substation. A fault on the bus, transformers, or a breaker failure event would outage the entire substation. The new substation will also accommodate future transmission expansion. |  |  |  | Ameren Services Company | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 138 | 0 | Planned | 16200000
A in MTEP21 | Central | AmerenIL | 18074 | Replace Jacksonville Industrial Park 138 kV Breakers | Jacksonville Industrial Park Breaker Replacement: Replace 138 kV breaker JCKI-138KV BT 1-2 BKR 1302 at Jacksonville Industrial Park Substation. | IL | IL | 2022-06-01 | Increased reliability |  |  |  | Ameren Services Company | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 138 | 0 | Planned | 1300000
A in MTEP21 | Central | AmerenIL | 18889 | Rebuild Hickok-North LaSalle 138 kV line (1659) | Rebuild the Hickok-North LaSalle 138 kV line for 2000 amps. | IL | IL | 2023-12-01 | Address an overload on the Hickok North LaSalle 138 kV line upon completion of the Statcom |  |  |  | Ameren Services Company | BRP |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Planned
A in MTEP21 | Central | AmerenIL | 19025 | New J815 Hickory Point Wind Generator Interconnection (Yvonne 138 kV switching Station) | Install new Yvonne 138 kV switching Station (J815 Hickory Point Wind Generator Interconnection) on the Austin-Taylorville S.-1545 line. | IL | IL | 2022-11-01 | Generator Interconnection |  |  |  | Ameren Services Company | GIP |  |  | 2022-11-01 | 2022-11-01 | 138 | 0 | Planned | 5700000
A in MTEP21 | Central | AmerenIL | 19026 | New J912 Christian County Solar Generator Interconnection (Pana 138 kV switching station) | New J912 Christian County Solar Generator Interconnection at Pana 138 kV switching station | IL | IL | 2023-10-01 | Generator Interconnection |  |  |  | Ameren Services Company | GIP |  |  | 2023-10-01 | 2023-10-01 | 138 | 0 | Planned | 900000
A in MTEP21 | Central | AmerenIL | 19085 | New Shelbyville S. 138 kV Ring Bus for PPI ISHI Load Addition | Rebuild the Shelbyville S. 138 kV bus to a 6 position ultimate ring bus. This will allow a new interconnection with PPI to serve their ISHI load. | IL | IL | 2022-06-01 | Customer load addition |  |  |  | Ameren Services Company | Other |  | Load Growth | 2022-06-01 | 2022-06-01 | 138 | 0 | Planned | 10000000
A in MTEP21 | Central | AmerenIL | 19345 | New Valmeyer 138 kV Substation | Construct Valmeyer 138 kV Substation Ring Bus and add a second 138/34.5 kV Transformer | IL | IL | 2024-06-01 | Increased reliability. Distribution driven project. |  |  |  | Ameren Services Company | Other |  | Reliability | 2024-06-01 | 2024-06-01 | 138 | 34.5 | Planned | 5900000
A in MTEP21 | Central | AmerenIL | 19826 | Upgrade Dupo Ferry 138 kV Substation | Replace overstressed breakers | IL | IL | 2025-12-01 | Replace overstressed breakers |  |  |  | Ameren Services Company | Other |  | Reliability | 2025-12-01 | 2025-12-01 | 138 | 0 | Planned
A in MTEP21 | Central | AmerenIL | 19956 | Rebuild Tanner-Jasper 138 kV line | Rebuild 23 miles to 2000 A. To coincide with Tanner 345/138 kV | IL | IL | 2022-12-01 | Baseline reliability |  |  |  | Ameren Services Company | BRP |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Planned | 7900000
A in MTEP21 | Central | AmerenIL | 19988 | New Roxford 345/138 kV Transformer Addition | Add second 345/138 kV transformer | IL | IL | 2023-12-01 | Increased reliability and system strength for customers. |  |  |  | Ameren Services Company | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 345 | 138 | Planned | 10200000
A in MTEP21 | Central | AmerenIL | 20079 | Rebuild Butler 69/12kV Substation | Rebuild Butler sub with new 5/6.25MVA 3ph transformer, relocate regulators, replace all switches | IL | IL | 2021-12-31 | Reliability |  |  |  | Wabash Valley Power Association, Inc. | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 69 | 12 | Planned | 1800000
A in MTEP21 | Central | AmerenIL | 20184 | New REOS 138 kV substation | Ring bus North of RS Wallace that ties together RS Wallace - Spring Bay and CAT2 - Hines 138 kV lines. | IL | IL | 2024-12-01 | Baseline reliability |  |  |  | Ameren Services Company | BRP |  |  | 2024-12-01 | 2024-12-01 | 138 | 0 | Planned | 8700000
A in MTEP21 | Central | AmerenIL | 20187 | Upgrade Chesterville 138 kV Substation | Add 2 line breakers | IL | IL | 2025-12-01 | Increased reliability. |  |  |  | Ameren Services Company | Other |  | Reliability | 2025-12-01 | 2025-12-01 | 138 | 69 | Planned | 1700000
A in MTEP21 | Central | AmerenIL | 20188 | New Upgrade Gibson City S 138 kV Substation | Add 5 position ring bus. | IL | IL | 2025-12-01 | Increased reliability |  |  |  | Ameren Services Company | Other |  | Reliability | 2025-12-01 | 2025-12-01 | 138 | 69 | Planned | 7000000
A in MTEP21 | Central | AmerenIL | 20191 | Upgrade Marion N 138 kV Substation | Add line breakers, disconnect switches and circuit switcher | IL | IL | 2024-12-01 | Increased reliability |  |  |  | Ameren Services Company | Other |  | Reliability | 2024-12-01 | 2024-12-01 | 138 | 69 | Planned | 8000000
A in MTEP21 | Central | AmerenIL | 20285 | Reconfigure Herrin East 138 kV substation | Install initial 4-position ring bus at the existing Herrin East substation location | IL | IL | 2022-12-01 | Increased reliability on the area distribution system and increased operating flexibility on the transmission system. |  |  | Replaces P15267 due to MOD submittal | Ameren Services Company | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 138 | 0 | Planned | 7500000
A in MTEP21 | Central | AmerenIL | 20365 | New Normal East 138/69 kV transformer | Install new 112 MVA, 138/69 kV Transformer | IL | IL | 2022-06-01 | Local load serving need |  |  |  | Ameren Services Company | Other |  | Load Growth | 2022-06-01 | 2022-06-01 | 138 | 69 | Planned | 2000000
A in MTEP21 | Central | AmerenIL | 20425 | Upgrade Holland-Kickapoo 138 kV | Remove CT limit as part of Kickapoo substation rebuild | IL | IL | 2022-12-01 | Increased reliability and operational flexibility |  |  |  | Ameren Services Company | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 138 | 0 | Planned | 500000
A in MTEP21 | Central | AmerenIL | 20465 | New Commodore 230 kV Interim Configuration | Interim configuration. 345/230 kV transformer at Commodore to serve the 230 kV St.John and West Frankfort area until the 230 kV to 345 kV line from Commodore to Jordan, and 138 kV line from Pinkneyville to St. John is finished. | IL | IL | 2021-10-05 | Increased reliability. |  |  |  | Ameren Services Company | Other |  | Reliability | 2021-10-05 | 2021-10-05 | 345 | 230 | Planned
A in MTEP21 | Central | AmerenIL | 21045 | Relocate ADM North-Mt. Zion 138 kV line (1616) | Relocate 0.6 miles of existing 138 kV ADM North-Mt. Zion Route 121-1616 to single circuit, single shaft steel poles. The entire section has distribution underbuild. | IL | IL | 2021-12-01 | The project was requested by the City of Decatur due to a Public Works project that is reconfiguring an intersection along Brush College Road. |  |  |  | Ameren Services Company | Other |  | Other Local Needs | 2021-12-01 | 2021-12-01 | 138 | 0 | Planned | 3500000
A in MTEP21 | Central | AmerenIL | 21325 | Rebuild Rossville-Vermilion 138 kV line (1305) | Rebuild the Rossville-Vermilion-1305 138 kV circuit with 2000 A summer emergency capability conductor. Also, install OPGW. | IL | IL | 2022-06-01 | Age and condition; OPGW |  |  |  | Ameren Services Company | Other |  | Age and Condition | 2022-06-01 | 2022-06-01 | 138 | 0 | Planned | 12800000
A in MTEP21 | Central | AmerenIL | 21585 | Rebuild Decatur East Main St-Route 51 Decatur 138 kV line (1416) | Rebuild the Decatur East Main St-Decatur Route 51 138 kV line. Scope of work includes: Replacement of existing OPGW with new OPGW, all to be installed in upper static position. Replacement remaining (31) wood pole structures; (28) will be replaced with single wood pole structures and 3 will be replaced with steel monopole structures. Reconductor with 2000A conductor. | IL | IL | 2022-12-01 | This project replaces the jointly-owned Ameren and Windstream 24-fiber OPGW with a new 72-fiber OPGW wholly owned by Ameren. Ameren's joint ownership agreement with Windstream expires at the end of 2022, and the terms of that agreement state that neither party can use the fiber optic cables included in that 24-fiber OPGW. Therefore, Ameren needs to replace that cable to maintain communications continuity in this area. Engineering identified that the existing structures on this line cannot handle the increased loading caused by the new OPGW. Engineering proposes replacing all the structures on this line with larger poles to handle this increased loading. Finally, Engineering proposes to replace the existing conductor with new conductors capable of carrying 2000 amps and Summer Emergency conditions. This provides greater operational flexibility but increasing the capacity of the line, reduces galloping related wear on the structures at the river crossing and removes aging infrastructure from the transmission system. |  |  |  | Ameren Services Company | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 138 | 0 | Planned | 4200000
A in MTEP21 | Central | AmerenIL, AmerenMO | 20193 | Replace Breakers Program - MTEP21 | Breaker Upgrades Requested by Maintenance. Ameren Transmission has an initiative to replace about 35 Hitachi breakers (HVB) on the system. There were eight (8) inadvertent transmission interruptions in the period of 2014-2021 due to HVB breakers, which is a high percentage for such a small population. In addition, modern breakers have spring trip (stored energy) and air close (compressor) mechanisms while HVB breakers have air trip and spring close mechanisms. Having an air trip mechanism makes HVB breakers dependent on a hydraulic system to trip, which is prone to problems. Also having a stored energy for close operation means that workers have to be alert to controlling this energy when working on HVB breakers to avoid any accident. | IL,MO | IL,MO | 2022-12-01 | Age and condition. Increased reliability. |  |  |  | Ameren Services Company | Other |  | Age and Condition | 2022-12-01 | 2024-12-01 | 345 | 138 | Proposed | 13500000
A in MTEP21 | Central | AmerenIL, AmerenMO | 20194 | Replace Relays Program - MTEP21 | Electromechanical Relay Upgrades Requested by System Protection | IL,MO | IL,MO | 2022-12-01 | Age and condition |  |  |  | Ameren Services Company | Other |  | Age and Condition | 2022-12-01 | 2024-12-01 | 345 | 138 | Proposed | 10350000
A in MTEP21 | Central | AmerenIL, AmerenMO | 20195 | Replace Pole and Insulator Program - MTEP21 | Pole and Insulator replacements requested by Maintenance. 432 structures in Missouri. 320 structures in Illinois. | IL,MO | IL,MO | 2022-12-01 | Age and Condition |  |  |  | Ameren Services Company | Other |  | Age and Condition | 2022-12-01 | 2024-12-01 | 345 | 138 | Proposed | 97500000
A in MTEP21 | Central | AmerenMO | 9830 | Reconductor Meramec-Joachim 138 kV line 2 | Meramec-Joachim-2 138 kV Line - Increase ground clearance to permit operation at 120 degrees C. Test the condition of the conductor, replace the deadends, shunt the splices and replace the hardware. | MO | MO | 2021-12-31 | Other-Increased reliability. Completion of NERC remediation. |  |  |  | Ameren Services Company | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 138 | Planned | 300000
A in MTEP21 | Central | AmerenMO | 17344 | Upgrade Berkeley 138 kV Substation | Replace 138 kV bus tie 1-2 and 2-3 breakers. Upgrade position to 2000A. | MO | MO | 2021-12-01 | Age and condition of existing breakers. |  |  |  | Ameren Services Company | Other |  | Age and Condition | 2021-12-01 | 2021-12-01 | 138 | 0 | Planned | 1300000
A in MTEP21 | Central | AmerenMO | 19827 | Upgrade Sioux 138 kV Substation-MTEP21 | Replace overstressed breaker 3H | MO | MO |  | Replace overstressed breaker |  |  |  | Ameren Services Company | Other |  | Age and Condition | 2025-12-01 | 2025-12-01 | 345 | 138 | Planned | 700000
A in MTEP21 | Central | AmerenMO | 19852 | New Sikeston 161 kV Substation | Construct new Comstock (Sikeston) 161kV breaker-and-a-half substation to interconnect Ameren's Miner-Sikeston line and Sikeston Board of Municipal Utilities' New-Madrid-Sikeston 161kV line. Construct new 161kV Reelfoot ring bus near New Madrid and extend SBMU's 161kV in/out of the ring bus. The City of New Madrid will install a 161/69kV xfmr to serve new industrial customer. | MO | MO | 2022-12-01 | Business development |  |  |  | Ameren Services Company | Other |  | Load Growth | 2022-12-01 | 2022-12-01 | 161 | 161 | Planned | 15200000
A in MTEP21 | Central | AmerenMO | 19968 | New Zachary-Maywood 345 kV Ring Bus for (J1025) | Zachary-Maywood 345 kV New Ring Bus for J1025 Generator Interconnection (Station name is Fabius) | MO | MO | 2022-06-01 | Generator Interconnection |  |  |  | Ameren Services Company | GIP |  |  | 2022-06-01 | 2022-06-01 | 345 | 0 | Planned | 9800000
A in MTEP21 | Central | AmerenMO | 19969 | New Belleau 138 kV Capacitor Bank | Install 120 Mvar capacitor bank at Belleau 138 kV | MO | MO | 2025-06-02 | Baseline Reliability |  |  |  | Ameren Services Company | BRP |  |  | 2025-06-02 | 2025-06-02 | 345 | 138 | Planned | 3500000
A in MTEP21 | Central | AmerenMO | 20065 | Replace New Bourbon 69 kV Breakers | Replace 69 kV brkrs B24, B25, B26, B39, & B40 at New Bourbon Sub. Also purchase a spare brkr. Install GPS clocks and wire to the microprocessor relays. | MO | MO | 2021-03-30 | Breaker reliability due to age and condition. GPS clocks necessary to match timeframe of operations. |  |  |  | Wabash Valley Power Association, Inc. | Other |  | Age and Condition | 2020-09-03 | 2020-09-03 | 69 | 0 | Planned | 1200000
A in MTEP21 | Central | AmerenMO | 20069 | New Salem Bulk DFR Installation | Install a new SEL data concentrator, Install GPS clocks and wire the GPS clocks to the microprocessor relays, Remove the relay 67 directional overcurrent tripping. | MO | MO | 2020-12-31 | Install a new SEL data concentrator, Install GPS clocks and wire the GPS clocks to the microprocessor relays, Remove the relay 67 directional overcurrent tripping elements that trip the transformer 69 kV breakers |  |  |  | Wabash Valley Power Association, Inc. | Other |  | Reliability | 2020-12-31 | 2020-12-31 | 69 | 12 | Planned | 100000
A in MTEP21 | Central | AmerenMO | 20070 | Upgrade Trail of Tears 69 kV Breakers | Replace the four oil filled 69 kV breakers at Trail of Tears to fix identified constraints for CT availability for the new bus differentials | MO | MO | 2022-09-05 | Equipment needed to add new bus differential relays. |  |  |  | Wabash Valley Power Association, Inc. | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 69 | 69 | Planned | 2800000
A in MTEP21 | Central | AmerenMO | 20072 | Rebuild Seminary to Park 69 kV Line | Upgrade 3.06 mi. 3/0ACSR to 477ACSR of 69kV Line T17 from Seminary B43 to Park tap switch 117. Add 48 fiber OPGW to entire 3.06 mile line. | MO | MO | 2022-08-10 | Reliability. Load transfers cause loading issues. |  |  |  | Wabash Valley Power Association, Inc. | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 69 | 69 | Planned | 2000000
A in MTEP21 | Central | AmerenMO | 20156 | New Galena 161 kV Capacitor Bank | Install 28.8 MVAR capacitor bank at Galena 161 kV | MO | MO | 2022-12-01 | Baseline reliability |  |  |  | Ameren Services Company | BRP |  |  | 2022-12-01 | 2022-12-01 | 161 | 0 | Planned | 900000
A in MTEP21 | Central | AmerenMO | 21125 | New Burns 345 kV Substation (J1145 Solar) | Construct 3 position ring bus on Montgomery-McCredie 345 kV line for 250 MW Show Me State Solar project J1145 | MO | MO | 2022-10-01 | Interconnection facilities for J1145 according to engineering agreement. |  |  |  | Ameren Services Company | GIP |  |  | 2022-10-01 | 2022-10-01 | 345 | 0 | Planned | 10100000
A in MTEP21 | Central | BREC | 3439 | New Ensor 161/69 kV Substation | Construct new 161/69 kV substation with 56 MVA transfomer. Include a 30 MVAR 69 kV capacitor | KY | KY | 2024-12-31 | Base case voltage issues and overloads during loss of one Daviess County 161/69 kV transformer. Capacitor needed to mitigate low voltages during loss of Reid to Daviess County 161 kV circuit. | Add third 161/69 kV transformer at Daviess County and add a capacitor at another location. |  |  | Big Rivers Electric Corporation | BRP | Not Shared |  | 2024-12-31 | 2024-12-31 | 161 | 69 | Proposed | 5800000
A in MTEP21 | Central | BREC | 18605 | New Hardinsburg 161kV Substation (J753) for solar Interconnection | Hardinsburg 161kV Substation (J753) for 100 MW solar Interconnection | KY | KY | 2023-07-01 | Hardinsburg 161kV Substation expansion (J753) for solar Interconnection |  |  |  | Big Rivers Electric Corporation | GIP |  |  | 2021-04-01 | 2021-04-01 | 161 | 0 | Proposed | 200000
A in MTEP21 | Central | BREC | 18606 | New Meade 161kV Substation (J762) for solar Interconnection | Meade County 161kV Substation modification for (J762) solar Interconnection | KY | KY | 2023-07-01 | Meade County 161kV Substation modification for 200 MW (J762) solar Interconnection |  |  |  | Big Rivers Electric Corporation | GIP |  |  | 2021-04-01 | 2021-04-01 | 161 | 0 | Proposed | 500000
A in MTEP21 | Central | BREC | 19006 | New Hartford 69 kV Tie line | 69 kV normally open tie from KU Hartford to a BREC tap near Beda. | KY | KY | 2020-11-03 | Provide emergency service to KU on an as-available basis. |  |  | IA will be provided when available | Big Rivers Electric Corporation | Other |  | Reliability | 2020-11-03 | 2020-11-03 | 69 | 0 | Proposed | 0
A in MTEP21 | Central | BREC | 21165 | New Maxon Load Addition | For the near term, the industrial customer is requiring 30 MW capacity. This load will be served on an interruptible basis through the expansion of an existing site on BREC's 69 kV system. The cost estimate for this phase is $1,200,000. For the long term, the industrial customer is expandable to require 60 MW capacity. This will require the addition of a 3.5 mile radial 161 kV circuit from BREC's McCracken substation to be overbuilt on an existing 69 kV circuit. The 69 kV circuit will be reconductored to allow for an alternate feed. The cost estimate for this phase is $10,200,000. | KY | KY | 2021-09-01 | Service for 60 MW load addition. |  |  |  | Big Rivers Electric Corporation | Other |  | Load Growth |  |  | 161 | 0 | Proposed | 11400000
A in MTEP21 | Central | BREC | 21387 | Hancock County Capacitor Bank Addition | Add a 35 MVar capacitor bank on the 69 kV bus at the existing Hancock County substation. | KY | KY | 2022-10-01 | Low voltage mitigation at Daviess County 161 kV bus for loss of Reid-Daviess 161 kV line. |  |  |  | Big Rivers Electric Corporation | BRP |  |  |  |  | 69 | 0 | Proposed | 500000
A in MTEP21 | South | CLECO | 13874 | Flagon Substation | Build a new 230 kV substation Tapped into the Donahue to Sherwood 230 kV line. Use the distribution in the area to move 16 MW from Beaver Creek substation. | LA | LA | 2020-05-01 | P7 contingencies on Donahue to Beaver Creek line 1 & 2 create low voltage at Beaver Creek substation in Summer Peak models. Building Flagon substation will allow more distribution flexibility in the area and reduce the load at Beaver Creek by at least 16 MW which will eliminate the low voltage condition associated with the P7 contingency. | This project would be an alternative to the Beaver Creek Double circuit rebuild project. |  |  | Cleco Power LLC | BRP |  |  | 2022-07-01 | 2022-07-01 | 230 | 0 | Proposed | 8130000
A in MTEP21 | South | CLECO | 21169 | Bayou Sale Cap Bank Move | Move the existing Bayou Sale 19.2 MVAR cap bank to Pelican 138 kV substation. | LA | LA | 2023-06-01 | P6 contingencies show low voltage issues and potential overloads. This project will help with the voltage issues and can be build before the longer term fix which is scheduled to be in-service by 2025. |  |  |  | Cleco Power LLC | BRP |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Proposed | 700000
A in MTEP21 | South | CLECO | 21207 | Slidell Airport Line Move | Slidell airport expansion requires moving our North Slidell to Tailsheek 230 kV line and North Slidell to Cane Bayou 230 kV line. | LA | LA | 2023-12-01 | Required for Airport Expansion at Slidell |  |  |  | Cleco Power LLC | Other |  | Other Local Needs | 2023-12-01 | 2023-12-01 | 230 | 0 | Proposed | 9800000
A in MTEP21 | West | CMMPA | 20166 | Delano_Municipal_Utilities_Substation_A_Transformer_Upgrade | Facility Type: Transformer Project Description: Replace the Sub A 10 MVA 69/12.47kV transformer with a new 12/16/20 MVA 69/12.47kV transformer. System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformers. The Sub A transformer is 27 years old built in 1993, rewound once, and reaching the end of its life. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed. Proposed Solution: Delano is planning to replace the Sub A transformer with a new 12/16/20 MVA 69/12.47kV transformer. This new transformer will meet the load growth forecasted for the city and provide reliability for its customers. Reconfiguration within the substation may also allow for more customers to be served in the event one of the two 69kV transformers is out of service. | MN | MN |  | System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformers. The Sub A transformer is 27 years old built in 1993, rewound once, and reaching the end of its life. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed. |  |  |  | Central Minnesota Municipal Power Agency | Other |  | Load Growth | 2021-04-05 | 2021-04-05 | 69 | 0 | Proposed | 1750000
A in MTEP21 | West | CMMPA | 20168 | Delano_Municipal_Utilities_Substation_B_Transformer_Upgrade | Facility type: Transmission System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformer. The Sub B transformer was original in 1970 and rewound in 1999. There has been another project submitted into MTEP 21 for the substation A transformer upgrade. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers in 2022 extra capacity is needed. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed. Proposed Solution: Delano is planning to replace substation B transformer with new 12/16/20 MVA 69/12.47kV transformer. This new transformer will meet the load growth forecasted for the city and provide reliability for its customers. Reconfiguration within the substation may also allow for more customers to be served in the event one of the two 69kV transformers is out of service. This solution also includes a new fire wall between the new transformers and additional distribution feeders for load transfer. | MN | MN |  | System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformer. The Sub B transformer was original in 1970 and rewound in 1999. There has been another project submitted into MTEP 21 for the substation A transformer upgrade. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers in 2022 extra capacity is needed. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed. |  |  |  | Central Minnesota Municipal Power Agency | Other |  | Load Growth | 2022-04-04 | 2022-04-04 | 69 | 0 | Proposed | 2500000
A in MTEP21 | West | CMMPA | 20169 | Delano_Municipal_Utilities_New_69_kV_Industrial_Park_Substation | Facility Type: Substation Project Description: Build a new 69kV substation to serve expected residential and future industrial park load growth. System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. The downtown substation does not have room for expansion. A new substation next to the GRE Crow River 115/69kV substation will need the future load growth needs of Delano. Proposed Solution: Delano is planning to build a new 69kV substation to serve expected residential and future industrial park load growth on the NW side of the city. Please also refer to the attachment of a DGR study for the new substation request under "Attachments". | MN | MN |  | System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. The downtown substation does not have room for expansion. A new substation next to the GRE Crow River 115/69kV substation will need the future load growth needs of Delano. |  |  |  | Central Minnesota Municipal Power Agency | Other |  | Load Growth | 2022-04-04 | 2022-04-04 | 69 | 0 | Proposed | 4100000
A in MTEP21 | Central | CWLD | 19805 | New UMC 69 kV Substation | Build a new UMC substation and add a new 69/13.8 kV transformer, build a 69 kV ring bus switch station, and connect two 69 kV lines to UMC ring bus. Ring bus will have four 69 kV breakers protecting two incoming 69 kV transmission lines, and will be connected to two parallel output 69 kV lines feeding two 69/13.8 kV transformers through their own 69 kV breakers. | MO | MO | 2025-09-01 | Improve reliability for University of Missouri-Columbia (UMC) due to expected load growth. | PSSE simulation showed a more reliable solution: Build a new UMC substation with a new transformer, build a ringbus, and provide additional 161 kV line to UMC. |  |  | City of Columbia, MO | Other |  | Reliability | 2025-09-01 | 2025-09-01 | 69000 | 13800 | Planned | 26000000
A in MTEP21 | Central | DEI | 20174 | New Sullivan 69 kV capacitor | Sullivan 69 kV - 19.8 Mvar capacitor | IN | IN |  | Reduced voltage support at Edwardsport Bk10 being replaced on emergent project | No cost effective alternatives |  |  | Duke Energy Corporation | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 69 | 0 | Proposed | 500000
A in MTEP21 | Central | DEI | 20181 | Replace Five Points 138 kV Circuit Breakers | Replace (5) 138kV oil circuit breakers with SF6 gas circuit breakers - 13803, 13804, 13809, 13813, and 138kV Bus tie breaker; 13803,04,13 were identified in 2020 as overdutied in the DEI short ckt analysis by P&C Eng'g | IN | IN | 2022-12-31 | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 138 | 0 | Proposed | 4987000
A in MTEP21 | Central | DEI | 20190 | Rebuild Monroe City Jct - Petersburg Jct 69 kV line | 6960 Pt 3 Rbld Monroe City Jct_Petersburg Jct w/ 477acsr - 6.25 miles. Reconductor 2.4 miles of circuit 13825 (structures #844-1162 to #844-1190/#844-3100) and 1.2 miles of circuit 13838 where they are double-circuited with 6960. Replace Monroe City Jct #1 and #2 switches and rename to 69-1 and 69-2. Rebuild the line at the Petersburg Jct (poles #821-1322 through 821-1327). | IN | IN | 2022-12-31 | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 138 | 69 | Proposed | 10010000
A in MTEP21 | Central | DEI | 20196 | New Rosston 69/12 kV substation | new sub to be fed from the 69182 ckt and will replace existing Whitestown 69/12kV sub in the 6983 ckt. | IN | IN |  | Distribution load growth | No alternative studied - required to serve load. |  |  | Duke Energy Corporation | Other |  | Load Growth | 2022-06-01 | 2022-06-01 | 69 | 12 | Proposed | 1337000
A in MTEP21 | Central | DEI | 20197 | Reconfigure Wabash 138 kV substation | Upgrade misc 69 kV station equipment and convert Wabash 138 kV straight bus to ring bus | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 138 | 69 | Proposed | 12570000
A in MTEP21 | Central | DEI | 20198 | Reconfigure Hortonville 345 kV substation | Replace line relays: 34504, 34527, 6917, 69142, 69155. Install equipment to convert 345 kV bus to ring bus config. | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 345 | 69 | Proposed | 1871000
A in MTEP21 | Central | DEI | 20199 | Reconfigure Tipton West 230 kV substation | reconfigure Tipton West 230 kV bus to ring configuration | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 230 | 0 | Proposed | 1864000
A in MTEP21 | Central | DEI | 20200 | Replace Noblesville Generating Station 138/69 kV equipment | replace 138/69/2.4kV Bk9; misc upgrades to 138kV relays and wave traps, etc. | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 138 | 69 | Proposed | 4328000
A in MTEP21 | Central | DEI | 20205 | Reconfigure Greenwood Clark Township 69 kV substation | expand ring bus and add 69165 line terminal at Clark Twnshp; build short line to HE Willard Green | IN | IN |  | This project will effectively increase capacity on the 69165 line by 5-10MVA to help serve increasing load in the Greenwood area and will also provide a reserve source to HE Willard Green. | Rebuild existing 69165 line |  |  | Duke Energy Corporation | Other |  | Reliability | 2021-12-08 | 2021-12-08 | 69 | 0 | Proposed | 4056000
A in MTEP21 | Central | DEI | 20206 | Rebuild Huntington 138 kV to Meridian Rd Jct 69 kV | 6923 Part 2 rebuild with 954acsr; replace switches at Erie Stone jct | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 69 | 0 | Proposed | 4006000
A in MTEP21 | Central | DEI | 20207 | Rebuild Loogootee Jct to Loogootee 69kV line | Rebuild transmission line 69194 from Loogootee Jct (pole #816-2001 through #816-2152). Approx 10.2 miles. Approx 152 poles. Replace Loogootee Jct #1, #2, and #3 switches. Replace H.E. Bramble #1 and #2 switches. | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 69 | 0 | Proposed | 13761000
A in MTEP21 | Central | DEI | 20208 | Rebuild Morgantown to Bean Blossom 69 kV line | Rebuild transmission line 6949 from Morgantown substation (pole #825-3122) to Bean Blossom substation (pole #825-3270) using light duty steel poles, 477 ACSR | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 69 | 0 | Proposed | 13353000
A in MTEP21 | Central | DEI | 20225 | Rebuild McKay Rd Jct. to H.E. Lewis Creek Jct. 69 kV line | Rebuild transmission line 6975 from McKay Rd Junction (pole #807-3096) to H.E. Lewis Creek Junction (pole #807-3168) using light duty steel poles, 477 ACSR conductor and OPGW. - 5.9 miles ; Replace two switches at McKay Rd Junction 2000A | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 69 | 0 | Proposed | 7244000
A in MTEP21 | Central | DEI | 20226 | Reconfigure Deedsville 345 kV substation | Reconfigure 345kV to ring bus. Replace various 345kV and 69kV transmission equipment including relays and OCBs | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 345 | 69 | Proposed | 7710000
A in MTEP21 | Central | DEI | 20227 | Reconfigure Middlefork 69 kV substation | Replace misc. 69kV OCBs and relays; replace 6910-01 line switch with 2000A; establish 69kV ring bus | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 69 | 0 | Proposed | 8713000
A in MTEP21 | Central | DEI | 20228 | Reconfigure Prescott 345 kV substation | Replace misc. 69kV OCBs and relays; establish 345kV ring bus | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 345 | 69 | Proposed | 7543000
A in MTEP21 | Central | DEI | 20230 | Rebuild Purdue NW Tap to Purdue to Cincinnati St. 138 kV line | Rebuild the 13820 line from the Purdue Northwest Tap to West Lafayette Purdue University to Cincinnati St. substation using 954 ACSR at 120 C | IN | IN | 2023-12-31 | (Replaces previous project 17485) With the new West Lafayette Airport sub getting placed in-service on the 13820 line between the Purdue Northwest Tap and West Lafayette Purdue subs, when there is a breaker failure that takes out bus 2 at Westwood, the line segments from the Purdue Northwest Tap to West Lafayette Airport to Purdue to Cincinnati St. are loaded to 99.7% or higher per the MTEP21 - 2023 sum peak _AA model. | short term ratings with operating mitigations; Change the 13806 and 13820 line terminals at Westwood, which moves the 13820 line to Bus 2 at Westwood and the 13806 line to Bus 1 at Westwood, but this does not help with N-1-1 contingencies |  |  | Duke Energy Corporation | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 138 | 0 | Proposed | 9580000
A in MTEP21 | Central | DEI | 20245 | J805 Gwynneville Solar | J805 Gwynneville Solar | IN | IN |  | GIA | GIA |  |  | Duke Energy Corporation | GIP |  |  | 2021-12-31 | 2022-02-15 | 345 | 0.6 | Planned | 7657657
A in MTEP21 | Central | DEI | 20246 | J829 Fairbanks Solar | J829 Fairbanks Solar | IN | IN |  | GIA | GIA |  |  | Duke Energy Corporation | GIP |  |  | 2022-08-19 | 2022-08-19 | 345 | 0.63 | Planned | 15447998
A in MTEP21 | Central | DEI | 20247 | Rebuild Lafayette S. to Shadeland 138 kV line | Rebuild 138100 ckt with 954ACSR@120C - 3.2 miles | IN | IN | 2023-06-01 | Line overload identified in MTEP20 analysis - (2) Cat. P7; Multiple P6 | situational short term ratings with post-contingent operating mitigations are no longer effective after 2025; additional 138 kV ckt across Lafayette is cost prohibitive |  |  | Duke Energy Corporation | BRP |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Proposed | 7500000
A in MTEP21 | Central | DEI | 20248 | Dresser 345kV Redundant Ckt Brkr Addition | Dresser 345kV Redundant Ckt Brkr Addition between Bk1 and Bk2 with fully redundant protection scheme per future P5 definition | IN | IN |  | MTEP20 contingency flow jumped up 64MVA (over 2019 results) which has violated the 15 minute 675MVA rating of Bk3; Violations are caused by the coincidental loss of Dresser 345/138kV Bks 1 and 2 due to misoperation / failure of their 345kV common ring bus breaker. Operating mitigation: open Dresser ckt breakers 13861 (towards Staunton - 249721,249685,1) and 13868 (towards Terre Haute S. 1st St. - 249721,249857,1) to alleviate OL until either Bk1 or Bk2 can be placed back in service. Project will insert a redundant breaker to eliminate the contingency. | Situational short term ratings with post-contingent operating mitigations were no longer effective in MTEP20 but are effective again in MTEP21. An automatic restoration scheme is being evaluated at this time and, if feasible, will become the preferred option to effectively eliminate this contingency. |  |  | Duke Energy Corporation | BRP |  |  | 2023-06-01 | 2023-06-01 | 345 | 0 | Proposed | 8000000
A in MTEP21 | Central | DEI | 20250 | DEI Bolivar to NIPS Templeton 69kV line | WVPA to construct new N.O. reserve 69kV line to existing NIPS Templeton sub from DEI Bolivar | IN | IN |  | WVPA planned project to supply an alternate feed to their existing NIPS Templeton sub to increase reliability | Contact WVPA's Tom Imel |  |  | Duke Energy Corporation | Other |  | Reliability | 2022-04-01 | 2022-04-01 | 69 | 0 | Proposed | 7000000
A in MTEP21 | Central | DEI | 20645 | New Greenfield Hastings Park 138 kV ring bus | Greenfield Hastings Park - establish a 3-breaker, 138kV, ring bus | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  |  | Duke Energy Corporation | Other |  | Reliability | 2021-10-01 | 2021-10-01 | 138 | 0 | Proposed | 4237000
A in MTEP21 | West | DPC | 19953 | Frenchville Tap N223 Rebuild | Rebuild 11.1 miles of the N-223 line from the N-122 tap to the XEL Ettrick substation with 4/0 conductor. | WI | WI | 2023-02-17 | Age and Condition |  |  |  | Dairyland Power Cooperative | Other |  | Age and Condition | 2023-04-14 | 2023-04-14 | 69 | 0 | Planned | 3848576.89
A in MTEP21 | West | DPC | 20136 | Pine Lake to Dunn Ethanol N4 Rebuild | This project is a mix of a rebuild of DPC’s existing 69 kV line in the area and construction on new right-of-way. The recommended plan in this area is to construct new transmission line with 477 ACSR conductor, a mix of replacement of existing line and new right-way from XEL’s Pine Lake transmission substation to the east towards the Dunn Ethanol distribution substation. The recommended plan will address the age and condition issues, constructing the line with new poles and 477 ACSR conductor. The plan will also address the longer tap lines to distribution substations with individual taps to all five distribution substations served from this line. Finally, building to the Dunn Ethanol distribution substation will provide backup service. | WI | WI | 2024-02-09 | DPC’s transmission line in this area was constructed in 1947 and has age and condition issues. |  |  |  | Dairyland Power Cooperative | Other |  | Age and Condition | 2024-02-09 | 2024-02-09 | 69 | 0 | Planned | 13051779.51
A in MTEP21 | South | Entergy-AR | 19907 | Moreland 161kV: Rebuild Substation | Wreck out the existing 20 MVA substation Transformer and associated bus and breakers and install a new substation consisting of 2-new 40 MVA substation transformers on the existing property to include two 161-13.8 KV, 40 MVA LTC transformers. Build 13.8kV low-side operating bus and transfer buses as per Entergy Substation Specifications including a 2000A bus tie breaker and bay connecting the two transformer busses. Install two 2000A main breaker bays and eight feeder breaker bays. | AR | AR |  | There is approximately 20 MVA of load at risk for the loss of the single transformer at Moreland substation. Currently there is load shifted from Moreland to Russellville to eliminate a real time overload on the existing transformer. |  |  |  | Entergy Arkansas | Other |  | Load Growth | 2022-12-30 | 2022-12-30 | 161 | 0 | M3_Long Lead Materials | 13400000
A in MTEP21 | South | Entergy-AR | 19908 | Cave City 161kV: Add 2nd Transformer | Add a 40 MVA 161/34.5kV LTC transformer in the existing substation. Install three 1200 Amp feeder breakers and a 1200 Amp bus tie breaker. | AR | AR |  | The existing 14 MVA transformer and regulator is projected to be loaded to 109% in the winter of 2023. |  |  |  | Entergy Arkansas | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 161 | 34.5 | M1_Final SPM or OOC | 8054670
A in MTEP21 | South | Entergy-AR | 19909 | 2021 EAL Asset Renewal Program | This project includes the EAL asset renewal projects that will be performed in 2021. | AR | AR | 2021-12-31 | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc. |  |  |  | Entergy Arkansas | Other |  | Age and Condition | 2021-12-30 | 2021-12-30 | 500 | 115 | M4_Pre-Construction | 27200000
A in MTEP21 | South | Entergy-AR | 19910 | 2022 EAL Asset Renewal Program | This project is for the EAL Asset Renewal Program that will be executed in 2022. | AR | AR | 2022-12-30 | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc. |  |  |  | Entergy Arkansas | Other |  | Age and Condition | 2022-12-30 | 2022-12-30 | 500 | 115 | M1_Final SPM or OOC | 19300000
A in MTEP21 | South | Entergy-AR | 21447 | Happy 115kV: New Switching Station (J1373) | Happy 115kV (J1373) is a new ring bus switching station tapped on the Searcy Price - Griffithville line section. Entergy Arkansas will install line taps into and out of the Happy 115kV switching station as well as line protection and breaker control relay upgrades, new RTU installation, and wave trap removal at the remote end Brinkley East and Searcy Price 115kV substations. Approximately 4.7 miles of underground fiber will be installed between Happy and Griffithville 115kV substation. | AR | AR | 2023-03-15 | This project is needed to provide a point of interconnection for the solar project J1373. |  |  |  | Entergy Arkansas | GIP |  |  | 2023-03-15 | 2023-03-15 | 115 | 0 | M1_Final SPM or OOC | 3717000
A in MTEP21 | South | Entergy-LA | 15605 | Frisco-Tezcuco 230kV: Upgrade Circuit 1 and 2 | Increase the rating of the Tezcuco to Frisco 230 circuit #1 and #2 to a minimum of 1925A (765 MVA). | LA | LA | 2021-12-01 | MISO identified thermal overloads on the Tezcuco to Frisco circuit #1 and #2 during generator interconnection and deliverability analysis. • Tezcuco to Frisco 230kV circuit #1 following the loss of Tezcuco to Frisco 230kV circuit #2 • Tezcuco to Frisco 230kV circuit #2 following the loss of Tezcuco to Frisco 230kV circuit #1 |  |  |  | Entergy | BRP |  |  | 2021-12-01 | 2021-12-01 | 230 | 0 | Proposed | 2200000
A in MTEP21 | South | Entergy-LA | 18228 | Golden Meadow to Clovelly 115 kV: Rebuild line | Rebuild the ~7 mile Golden Meadow to Clovelly 115 kV line to 230 kV specifications. | LA | LA |  | Enhanced Reliability. The P1.3 loss of the Barataria 230/115 kV autotransformer creates loadings on Clovelly to Golden Meadow over 90%. Increase reliability to the area. Hurricane damage to the other source into the region has elevated the need for this project. |  |  |  | Entergy | Other |  | Reliability | 2022-02-28 | 2022-02-28 | 115 | 0 | Proposed | 86300000
A in MTEP21 | South | Entergy-LA | 19957 | Lake Arthur 69 kV Switch Upgrade | Replace switch 732 at Lake Arthur with a motorized load break switch that has whips and bottles. Move the Normally Open point from switch 8873 to switch 732 so that Lake Arthur 69 kV station is fed out of Lawtag 69 kV station. | LA | LA | 2022-06-01 | This project is needed to mitigate N-0 voltage violation at Lake Arthur 69 kV bus and to maintain compliance with Entergy’s Transmission Planning Criteria. |  |  |  | Entergy | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 69 | 0 | Proposed | 706000
A in MTEP21 | South | Entergy-LA | 19987 | Nelson 230/138 kV Relay Improvement SPOF | Dual Battery installations or monitoring sufficient to FERC 754 guidelines at Nelson 230 kV and 138 kV stations. Install and verify high speed dual primary protection on the GSU for all power plants interconnected at Nelson 230 kV and 138 kV substations | LA | LA | 2022-06-01 | NERC TPL-001-4 violations observed for a P5 contingency at Nelson including thermal overloads on the Carlyss 230-138 kV Autotransformer and the Sphere to Mossville 69 kV line. |  |  |  | Entergy | BRP |  |  | 2023-12-01 | 2023-12-01 | 230 | 138 | Proposed | 17900000
A in MTEP21 | South | Entergy-LA | 20039 | 2021 ELL Asset Renewal Program | This project is for the ELL Asset Renewal Program that will be executed in 2021. | LA | LA |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | Entergy | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 500 | 69 | Proposed | 96480929
A in MTEP21 | South | Entergy-LA | 20040 | 2022 ELL Asset Renewal Program | This project is for the ELL Asset Renewal Program that will be executed in 2022 | LA | LA |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | Entergy | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 500 | 69 | Proposed | 42100000
A in MTEP21 | South | Entergy-LA | 20045 | Northline 230 kV: New Substation | Northline 230 kV distribution substation will cut in between the existing Addis and Cohen 230 kV stations. | LA | LA | 2024-06-01 | Distribution System Load Growth. |  |  |  | Entergy | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 230 | 0 | Proposed | 42800000
A in MTEP21 | South | Entergy-LA | 20122 | 2021 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2021 | LA | LA |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | Entergy | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 230 | 69 | Proposed | 5900000
A in MTEP21 | South | Entergy-LA | 20124 | 2022 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2022 | LA | LA |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | Entergy | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 230 | 69 | Proposed | 4500000
A in MTEP21 | South | Entergy-LA | 20306 | Adams Creek Relay upgrades (J830,J868,J908) | Relay upgrades at Adams Creek/Bogalusa 500 kV. | LA | LA |  | Identified by MISO for NRIS/ERIS for the interconnection customers J830, J868, and J908. |  |  |  | Entergy | GIP |  |  | 2021-12-15 | 2021-12-15 | 500 | 0 | Planned | 417756
A in MTEP21 | South | Entergy-LA | 20307 | Par 115 kV Station(J1184) | Construct a 115 kV substation named Par between the existing Franklinton and Holton 115 kV substations. | LA | LA |  | This station is being constructed to accommodate the interconnection of a solar facility (J1184). |  |  |  | Entergy | GIP |  |  | 2021-03-02 | 2021-03-02 | 115 | 0 | M5_In Service | 4050923
A in MTEP21 | South | Entergy-LA | 20585 | J1142 Generator Interconnection at Vacherie 230 kV | Facilities required for the interconnection of J1142 at the existing Vacherie 230 kV substation. | LA | LA |  | This construction at the existing Vacherie 230 kV substation is to accommodate the interconnection of a solar facility (J1142) |  |  |  | Entergy | GIP |  |  | 2021-03-29 | 2021-03-29 | 230 | 0 | M5_In Service | 4300000
A in MTEP21 | South | Entergy-LA | 20628 | J1158 Generator Interconnection at Vacherie 230 kV | Facilities required for the interconnection of J1158 at the existing Vacherie 230 kV substation. | LA | LA |  | This construction at the existing Vacherie 230 kV substation is to accommodate the interconnection of a solar facility (J1158) |  |  |  | Entergy | GIP |  |  | 2022-12-01 | 2022-12-01 | 230 | 0 | Proposed | 40000
A in MTEP21 | South | Entergy-LA | 21085 | Sugar House 230 kV: New Station | Entergy is proposing to construct a new 230 kV substation (Sugar House 230 kV Substation) which will serve an industrial customer’s 50 MW of new load in Port Allen, LA. The new lines into the Sugar House substation will be cut in and out (~.7 miles total) of the existing Formosa to Placid 230 kV line. The Sugar House 230 kV station will be constructed as a 3 breaker ring bus. Relocation of a portion of the existing 138 kV line that shares right of way with the 230 kV line will also be part of this project. | LA | LA |  | Entergy has received a request from a customer interested in adding new load to a new station on the transmission system. |  |  |  | Entergy | Other |  | Load Growth | 2022-12-31 | 2022-12-31 | 230 | 0 | Planned | 20100000
A in MTEP21 | South | Entergy-LA | 21525 | Sullivan 230 kV: New Station, Southport to Sullivan 230 kV Line upgrade | Construct new 230 kV station to be cut into the Southport to Joliet 230 kV line. Upgrade the Southport to Sullivan 230 kV line. | LA | LA | 2023-06-01 | The Sullivan station will be dedicated to serve New Orleans Sewerage and Water Board load. The Southport to Sullivan 230 kV upgrade is driven by NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. In 2023 summer the P2.3 Internal Breaker Fault of a Ninemile breaker will cause overloads on the Southport to Sullivan 230kV line. |  |  |  | Entergy | BRP |  |  | 2023-06-01 | 2023-06-01 | 230 | 0 | M2a_Pre-Project Approval | 27100000
A in MTEP21 | South | Entergy-LA, Entergy-MS | 20058 | Baxter Wilson - Perryville 500 kV terminal equipment upgrade | Upgrade the following terminal equipment at Baxter Wilson SES SWYD (Perryville Line Bay) to a minimum through-path rating of 1940 MVA: J2217, J2219, Line Trap, SEL321. | MS | LA |  | Enhanced Reliability. P1.1 Loss of Grand Gulf generator causes thermal loading of 98% in 2021 Winter. P3 loss of Grand Gulf coupled with loss of the McAdams to Lakeover 500 kV line requires over 2500 MW of generation redispatch to mitigate in 2025 Winter. |  |  |  | Entergy Mississippi | Other |  | Reliability | 2022-12-15 | 2022-12-15 | 500 | 0 | Proposed | 1110925
A in MTEP21 | South | Entergy-MS | 13995 | Mannsdale 230kV Substation | Build new Mannsdale 230kV substation in operating and transfer configuration. Include appropriate high-side fault protection. Install two (2) – 40 MVA, 230 kV-13.8kV, LTC, transformers including high-side circuit switchers to operate at 12.47kV. Install two (2) – 2,000 amp, 13.8kV, main breakers. Install eight (8) 1200 amp, 12.47 kV, breaker bays and equip with six (6) breakers; three (3) breakers to be served by T-1, and three (3) to be served by T-2. Install control house and all necessary relaying equipment. | MS | MS |  | The service area of the planned Mannsdale substation is a portion of west Madison county experiencing growth rates of 3% or more with several known block load subdivisions planned in the near future and multiple tracks for potential build out. It is currently being served by circuits from Flora, Bozeman, and Lake Castle substations at 3 to 7 line miles away. There is some transfer capability between circuits for contingency conditions but it is limited by voltage decay due to heavy loading and distance. Beginning in 2020 feeder configurations will have to be switched to non-optimal reliability configurations due to load growth in the area. |  |  |  | Entergy Mississippi | Other |  | Load Growth | 2025-06-01 | 2025-06-01 | 230 | 0 | Planned | 32200000
A in MTEP21 | South | Entergy-MS | 15848 | Jayess Loop Project | Rebuild L523 (Norfield SS to Little Creek) with sufficient ACSR conductor. Tap L549 (Jayess SS to Jayess) with a 115kV GOAB, tap L523 with a 115kV GOAB and build a new 115kV transmission line from Jayess GOAB to Little Creek GOAB. Build a new 115kV breaker switching station at Jayess and build a new 115kV breaker switching station at Norfield. | MS | MS | 2024-05-01 | Current radial transmission service violates MW-Mile planning criteria. |  |  |  | South Mississippi Electric Power Association | Other |  | Reliability | 2024-05-01 | 2024-05-01 | 115 | 0 | Proposed | 14660000
A in MTEP21 | South | Entergy-MS | 15850 | Olive Oil Loop Project | Rebuild L546 (Pisgah GOAB to Magee Road SS) with sufficient ACSR conductor. Rebuild L547 (Arlington GOAB to Arlington) with sufficient ACSR conductor. Tap L547 with a 115kV GOAB, tap L576 (Magee Road SS to Olive Oil) with a 115kV GOAB and build a new 115kV transmission line from Arlington GOAB to Olive Oil GOAB. Build a new 115kV breaker switching station at Arlington. | MS | MS | 2024-12-01 | Current radial transmission service violates MW-Mile planning criteria. |  |  |  | South Mississippi Electric Power Association | Other |  | Reliability | 2024-12-01 | 2024-12-01 | 115 | 0 | Proposed | 12106000
A in MTEP21 | South | Entergy-MS | 20055 | McAdams 230 kV: Relay Improvement SPOF | Project addresses Relay Single Point of Failure at McAdams 230 kV substation by adding or replacing bus differential protection on the 230kV buses, adding or replacing bus potential transfer panel, replacing two (2) OCBs, breaker control panel and CCVTs. | MS | MS | 2022-06-01 | The P5 loss of the McAdams 230kV bus due to a failed bus differential relay causes thermal overloads on the S. Grenada to Elliot 115kV line. There is also the potential for ~2000 MW of generation trip to occur for a 3PH fault on the McAdams 230 kV bus with non-redundant relay failure (TPL-001-4 category 2 stability extreme event). This project improves relay protection deficiencies at the McAdams 230 kV substation. |  |  |  | Entergy Mississippi | BRP |  |  | 2023-06-01 | 2023-06-01 | 230 | 0 | Proposed | 4600000
A in MTEP21 | South | Entergy-MS | 20057 | Franklin 115 kV: Relay Improvement SPOF | Install dual primary protection with independent CT and PT winding inputs on the Franklin 115 kV bus. Dual battery installations or monitoring sufficient to meet FERC 754 guidelines. | MS | MS | 2022-06-01 | NERC TPL-001-4 violations observed for a P5 contingency at Franklin 115 kV substation. Failure of the 115kV bus differential relay to clear a fault causes the loss of the Franklin 115kV and 500kV busses. This results in widespread thermal and voltage issues in Southwest Mississippi. |  |  |  | Entergy Mississippi | BRP |  |  | 2023-06-01 | 2023-06-01 | 115 | 0 | Proposed | 1700000
A in MTEP21 | South | Entergy-MS | 20060 | 2021 EML Asset Renewal Program | This project includes the EML asset renewal projects that will be performed in 2021. | MS | MS |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc. |  |  |  | Entergy Mississippi | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 500 | 115 | Proposed | 29069307
A in MTEP21 | South | Entergy-MS | 20061 | 2022 EML Asset Renewal Program | This project includes the EML asset renewal projects that will be performed in 2022. | MS | MS |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc. |  |  |  | Entergy Mississippi | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 500 | 115 | Proposed | 30477959
A in MTEP21 | South | Entergy-MS | 20308 | Franklin Relays Upgrade (J830 J868 J908) | Relay upgrade at Franklin 500 kV. | MS | MS |  | Identified by MISO for NRIS/ERIS for the interconnection customers J830 J868 J908. |  |  |  | Entergy Mississippi | GIP |  |  | 2021-12-15 | 2021-12-15 | 500 | 0 | Planned | 900000
A in MTEP21 | South | Entergy-TX | 19853 | Fork Creek 138kV Station Upgrade | Upgrade of existing substation with addition of 138kV line breakers for through-bus operation. | TX | TX |  | Increase transmission system reliability, improve response to outage conditions, reduce time for switching operations. |  |  |  | East Texas Electric Cooperative Inc. | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 138 | 0 | Planned | 900000
A in MTEP21 | South | Entergy-TX | 19954 | Newton 138 kV Station | Convert existing radial substation to looped substation and install 138/69 kV transformer. | TX | TX |  | Increase transmission system reliability, improve customer reliability, improve response time to outages, reduce time required for switching operations. |  |  |  | East Texas Electric Cooperative Inc. | Other |  | Reliability | 2023-04-01 | 2023-04-01 | 138 | 69 | Planned | 5300000
A in MTEP21 | South | Entergy-TX | 20042 | 2021 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2021. | TX | TX |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | Entergy | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 500 | 69 | Proposed | 22100000
A in MTEP21 | South | Entergy-TX | 20043 | 2022 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2022 | TX | TX |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | Entergy | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 500 | 69 | Proposed | 32500000
A in MTEP21 | South | Entergy-TX | 20067 | Southline 138 kV: New Substation | Southline 138 kV substation is a distribution station that will be cut into the Cleveland to Jayhawker 138 kV line. | TX | TX | 2023-12-01 | Distribution system load growth |  |  |  | Entergy | Other |  | Load Growth | 2023-12-01 | 2023-12-01 | 138 | 0 | Proposed | 34800000
A in MTEP21 | South | Entergy-TX | 20073 | Ponderosa 230 kV: Install Power Transformer | Install power transformer at the Ponderosa 230 kV substation. There are no power transformers currently installed at Ponderosa. | TX | TX | 2024-06-01 | Distribution system load growth |  |  |  | Entergy | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 230 | 0 | Proposed | 23500000
A in MTEP21 | South | Entergy-TX | 20405 | J1030 Station Interconnection Project | This project is to construct the interconnection station for the solar project J1030 on the Poco to Menard 138 kV line. | TX | TX |  | This project is to support the interconnection of solar project J1030 on the Poco to Menard 138 kV line. |  |  |  | Entergy | GIP |  |  | 2023-01-01 | 2023-01-01 | 138 | 0 | Proposed | 7150200
A in MTEP21 | Central | GLH | 19746 | Rebuild Joppa-Shawnee 161 kV line Ckt 2 | Rebuild the GridLiance Heartland portion of the Joppa - Shawnee 161 kV ckt 2 line | IL,KY | IL,KY | 2021-12-31 | After purchasing the transmission facilities in March 2020, GridLiance Heartland as part of our integration of facilities into our Operatons plan performed a LiDAR survey and identified clearance issues with the line and found a significant number of the structures require replacement on this circuit. Typically these issues would be indentified in a maintenance plan and submitted for future MTEP cycles but GridLiance has identified the issues on this line as critical. GridLiance has been working with MISO RC and SERC to resolve the clearance issues. The 2010 NERC Alert was not previously addressed by former TOs of these facilities and has just been identified by GridLiance as an issue. GridLiance determined its mitigation is to rebuild the line in consideration of the clearance issues and the overall poor condition of a majority of the structures with an age of the facilities (>60 years). GridLiance must start immediately to address the reliability issues. |  |  |  | Gridliance | Other |  | Age and Condition | 2022-03-01 | 2022-03-01 | 161 | 0 | Planned | 11000000
A in MTEP21 | Central | GLH | 20001 | Rebuild Joppa-Shawnee 161 kV Ckt 3 | Rebuild the GridLiance Heartland portion of Joppa-Shawnee 161 kV Ckt 3 | IL,KY | IL,KY |  | Age and condition of line |  |  |  | Gridliance | Other |  | Age and Condition | 2023-06-01 | 2023-06-01 | 161 | 0 | Planned | 11700000
A in MTEP21 | Central | GLH | 20004 | Rebuild Joppa-Shawnee 161 kV Ckt 4 | Rebuild the GridLiance Heartland portion of Joppa-Shawnee 161 kV Ckt 4 | IL,KY | IL,KY |  | Age and condition of line |  |  |  | Gridliance | Other |  | Age and Condition | 2023-06-01 | 2023-06-01 | 161 | 0 | Planned | 11700000
A in MTEP21 | Central | GLH | 20005 | Rebuild Joppa-Shawnee 161 kV Ckt 1 | Rebuild GridLiance Heartland portion of Joppa-Shawnee 161 kV Ckt 1. | KY,IL | KY,IL |  | Age and condition of line |  |  |  | Gridliance | Other |  | Age and Condition | 2023-06-01 | 2023-06-01 | 161 | 0 | Planned | 14700000
A in MTEP21 | West | GRE | 18865 | Square Butte - Stanton 230 kV Upgrade (J302/J503) | Upgrade Square Butte - Stanton 230 kV line for generation interconnections J302 & J503. | ND | ND | 2021-07-10 | Generation interconnections J302 & J503. |  |  |  | Great River Energy | GIP |  |  | 2021-07-10 | 2021-07-10 | 230 | 0 | Proposed | 6379446
A in MTEP21 | West | GRE | 20139 | Winthrop McLeod - Winthrop Xcel (MC-WW) 69 kV Rebuild | Rebuild MC-WW (9 miles) to upgradable 69kV with T2 capable of 1500-1600 amps. Remove SS2950 Winthrop tap switch. | MN | MN | 2024-05-01 | The existing MC-WW line is lossy and introduces a significant voltage drop causing a weaken/marginal voltage at McLeod’s Highland substation during contingencies. System analysis show that the existing transmission system doesn’t have capacity to serve additional load that may come to connect to the 69 kV system. Rebuilding this transmission line with a less lossy line strengths voltage profile and make additional capacity available in the 69 kV system. |  |  |  | Great River Energy | Other |  | Reliability | 2024-05-01 | 2024-05-01 | 69 | 0 | Proposed | 6616829
A in MTEP21 | West | GRE | 20141 | Decoria - Decoria Tap - Stoney Creek (BE-MD) 69 kV Rebuild | Rebuild BE-MD segments 1 and 2 (4.02 miles) and SS2826 to 69kV with T2 1200 amp capable conductor. | MN | MN | 2023-04-28 | Poor reliability. |  |  |  | Great River Energy | Other |  | Reliability | 2023-10-27 | 2023-10-27 | 69 | 0 | Proposed | 3015848.74
A in MTEP21 | West | GRE | 20151 | Milaca Breaker Addition 69 kV | Move ECE’s Milaca delivery points from the auxiliary bus onto the main bus and with circuit breaker protection. | MN | MN | 2021-12-31 | The Milaca – Ogilvie 69 kV line is 12.7 miles, 170°F, 36.2/55.6 MVA line that is limited by jumpers (30.1/45.7 MVA). During summer peak loading, the “PG” (Milaca – Ogilvie 69 kV) line will overload when Milaca 5NB1 trips. This is based off existing summer peak loads and does not depend on load growth to achieve the need. |  |  |  | Great River Energy | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 69 | 0 | Proposed | 419407.71
A in MTEP21 | West | GRE, MP | 20143 | Wing River 230 kV Ring Bus | Convert the 230 kV portion of the Wing River substation into a ring bus. | MN | MN | 2022-08-26 | Avoid excessive tripping of BES elements for both normal and abnormal fault clearing scenarios. |  |  |  | Great River Energy | Other |  | Reliability | 2022-08-26 | 2022-08-26 | 230 | 0 | Proposed | 3722667.74
A in MTEP21 | West | GRE, MRES | 17996 | Willmar 230/115 kV Transformer | Add a 230/115 kV LTC transformer at Willmar substation. | MN | MN | 2022-05-01 | Low voltage during loss of Morris - Morris OTP 115 kV line. Better load sharing between Priam 115/69 kV transformer and Willmar 230/69 kV transformer. |  |  |  | Great River Energy | Other |  | Reliability | 2022-05-01 | 2022-07-19 | 230 | 115 | Proposed | 12285046.31
A in MTEP21 | West | GRE, MRES | 20148 | Appleton - Benson (AG-AB) 115 kV Line | Construct about 27 miles of 115 kV transmission line from Appleton to GRE’s AG-BK line and about 1.75-mile 115 kV transmission line from AG-BK line to Benson Muni substation with associated tap switch, distribution sub, and retirement projects. | MN | MN | 2026-07-31 | This project is needed for the following reasons: 1. Accommodate future load growth in the Benson and other areas along the 115-kV transmission system 2. Improve load serving capability of the 41.6 kV and 115 kV transmission system 3. Address future NERC standard reliability violations, such as contingency low voltage concerns in the 115-kV system 4. Address existing N-2 contingency voltage collapse cases it the 115-kV system |  |  |  | Great River Energy | Other |  | Reliability | 2026-07-31 | 2026-07-31 | 115 | 0 | Proposed | 34773673
A in MTEP21 | West | GRE, MRES | 20608 | Worthington Substation | This project is for the construction of a 69/12.47 kV substation, preliminary referred to as the New Worthington Sub, on the east side of Worthington, MN. In addition, MRES and GRE are recommending a two-stage capacitor bank (2 x 7.0 MVAR) to address transmission needs and improve operations. | MN | MN | 2022-11-01 | Based on the planned customer expansions, the Worthington load is expected to exceed capacity capabilities of the WPU transmission-to-distribution system (along with inadequacies in the distribution system to backup this load effectively). So, additional load service is necessary. GRE and MRES have concluded that the addition of the New Worthington Sub is necessary. With the transmission system exceeding its voltage support capabilities, some investment in the transmission system is necessary. For that, we have concluded that capacitor banks should be included in that substation addition. |  |  |  | Missouri River Energy Services (MRET) | Other |  | Reliability | 2022-11-01 | 2022-11-01 | 69 | 0 | Proposed | 4800000
A in MTEP21 | Central | IPL | 20134 | New Stout 345 kV Breaker | Add one 345 kV breaker to form a ring bus at the Stout S substation. | IN | IN | 2022-12-31 | Adding the 345 kV breaker to form a ring bus allows for the Stout to Thompson and Stout to Hanna 345 kV lines to remain in service for the Stout 345-138 kV auto-transformer contingency. This allows for the removal of the operating procedures needed for P6 contingency thermal overloads that are the result of the loss of the Stout 345-138 kV auto-transformer combined with other elements. |  |  |  | Indianapolis Power & Light Company | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 345 | 0 | Planned | 3150400
A in MTEP21 | Central | IPL | 20137 | New Guion 345/138 kV transformer No. 3 | One (1) new third 500 MVA auto transformer is scheduled to be installed at Guion substation. This project is needed to increase import capability and plan for the possible unavailability of long lead time equipment. The project includes three (3) new 345 kV breakers, two (2) replacement 345kV breakers, two (2) 138 kV breakers, and terminal equipment including disconnect switches, relays, etc. | IN | IN | 2023-12-31 | Removes the need for numerous operating guides for P6 contingencies. |  |  |  | Indianapolis Power & Light Company | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 345 | 138 | Planned | 13376000
A in MTEP21 | West | ITCM | 17968 | Thisius 161/69kV Substation | ITCM will construct a 161:69kV substation at the crossing of the Huntley – Freeborn 161kV and Huntley – Walters 69kV circuits. | MN | MN | 2023-05-31 | Low voltage on the 69kV system in the area and to increase operational flexibility in the Albert Lea area |  |  | This project is being brought forward in MTEP21 in response to GRE withdrawing their capacitor bank project. | ITC Midwest | Other |  | Reliability | 2023-05-31 | 2023-05-31 | 161 | 69 | Planned | 7888877
A in MTEP21 | West | ITCM | 19925 | Albia-Melrose 69kV Rebuild | The majority of the Albia to Melrose 69kV line is near end of life and in poor condition. The line between the Albia and Melrose substations (~17.25 miles) will be rebuilt to current 69kV standards. All new equipment should be rated at 600A or higher minimum summer normal rating. | IA | IA | 2024-12-31 | The majority of the Albia to Melrose 69kV line is near end of life and in poor condition. |  |  |  | ITC Midwest | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 16293244
A in MTEP21 | West | ITCM | 19926 | Osceola North-Woodburn Jct 69kV Rebuild | The majority of the Osceola North to Woodburn 69kV line is near end of life and in poor condition. The line between the Osceola North, Osceola Rec, and Woodburn Jct. substations (~9.57 miles) will be rebuilt to current 69kV standards. All new equipment should be rated at 600A or higher minimum summer normal rating. | IA | IA | 2024-12-31 | The majority of the Osceola North to Woodburn 69kV line is near end of life and in poor condition. |  |  |  | ITC Midwest | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 8964000
A in MTEP21 | West | ITCM | 19928 | Marion-Old Settlers 115kV Ckt#2 | To better serve the Northeast Cedar Rapids load pocket, ITC will energize the second circuit on the Marion – Old Settlers 115kV structures and terminate it into Marion & Old Settlers substations. | IA | IA | 2025-12-31 | To better serve the Northeast Cedar Rapids load pocket, ITC will energize the second circuit on the Marion – Old Settlers 115kV structures and terminate it into Marion & Old Settlers substations. |  |  |  | ITC Midwest | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 115 | 115 | Planned | 4232578
A in MTEP21 | West | ITCM | 19931 | Dickinson County-Triboji 161kV Sag Remediation | Remove all existing sag limits on Dickinson County – Triboji 161 kV line to raise 636 ACSR to full summer conductor rating at 212 F (953/953/953 amps SN/SE/SSE 266/266/266 MVA SN/SE/SSE). | IA | IA | 2022-12-31 | Remove all existing sag limits on Dickinson County – Triboji 161 kV line to raise 636 ACSR to full summer conductor rating at 212 F (953/953/953 amps SN/SE/SSE 266/266/266 MVA SN/SE/SSE). |  |  |  | ITC Midwest | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 161 | 161 | Planned | 369600
A in MTEP21 | West | ITCM | 19993 | Triboji 69kV Cap Bank | ITC will install a 11.25MVAR Effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor on the Triboji J2 bus. All new substation equipment should have a minimum rating of 1200A. | IA | IA | 2023-12-31 | Low voltage on the 69kV system in the Triboji area under contingency. |  |  |  | ITC Midwest | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 69 | 69 | Planned | 813960
A in MTEP21 | West | ITCM | 19995 | West Union 69kV Cap Bank | ITC will install a 11.25MVAR Effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor on the West Union J2 bus. All substation equipment should have a minimum rating of 1200A. | IA | IA | 2023-12-31 | Low contingency voltage in the West Union area. |  |  |  | ITC Midwest | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 69 | 69 | Planned | 812280
A in MTEP21 | West | ITCM | 19996 | Monona 69kV Sub Rebuild & Cap Bank Addition | ITC rebuild the Monona 69kV substation and install a 11.25MVAR effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor at a new Monona Substation adjacent to the existing site. All substation equipment should have a minimum rating of 1200A. This will allow for two 69kV buses and the cap bank installation at the new Monona site improving operational flexibility and addressing voltage concerns in the area. | IA | IA | 2023-12-31 | Low voltage on the 69kV system in the area under contingency. |  |  |  | ITC Midwest | Other |  | Reliability | 2022-12-31 | 2023-12-31 | 69 | 69 | Planned | 1152000
A in MTEP21 | West | ITCM | 20025 | Bethel-Tripoli 69kV Rebuild | The majority of the Bethel-Tripoli 69kV line is near end of life and in poor condition. The line between the Bethel substation and Fredericksburg Tap (~8 miles) will be rebuilt to current 69kV standards. All new equipment should be rated 600A or higher minimum summer normal rating. | IA | IA | 2024-12-31 | The majority of the Bethel-Tripoli 69kV line is near end of life and in poor condition. |  |  |  | ITC Midwest | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 7740000
A in MTEP21 | West | ITCM | 20026 | Osage Jct-Rice 69kV Rebuild | The majority of the Osage JCT-Rice 69kV line is near end of life and in poor condition. The line between Osage JCT and Douglas Tap (~13.9 miles) and Riceville to Rice (~9.8 miles) will be rebuilt to current 69kV standards. All new line equipment should be rated 600A or higher. | IA | IA | 2024-12-31 | The majority of the Osage JCT-Rice 69kV line is near end of life and in poor condition. |  |  |  | ITC Midwest | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 22980000
A in MTEP21 | West | ITCM | 20027 | Meservey 69kV Tap Retirement | Retire ~6.9 miles of 69kV line to the IPL owned Meservey substation. Also remove line switches 4122 and 4123. All poles with underbuild should be topped per underbuild owner specification. All necessary outages should be coordinated with IPL. | IA | IA | 2022-12-31 | The Meservey 69kV tap will no longer be needed. Customer Requested. |  |  |  | ITC Midwest | Other |  | Other Local Needs | 2022-12-31 | 2022-12-31 | 69 | 69 | Planned | 420000
A in MTEP21 | West | ITCM | 20028 | Emery-6th Ave 69kV Rebuild | Beginning at where the double circuit ends (~0.35 miles outside Emery) - IPL’s 6th Ave substation will be rebuilt (~5.54 miles of line) to current 69kV standards. All new line should be rated 1200A or higher. | IA | IA | 2024-12-31 | The majority of the Emery 6th Ave 69kV line is near end of life and in poor condition. |  |  |  | ITC Midwest | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 7200000
A in MTEP21 | West | ITCM | 20029 | Southern Iowa New 161kV line and Breaker Stations | ITC will be building about 29 miles of 161kV line from CIPCO’s Winterset Jct. to Osceola’s new substation. This new line will be constructed using T2 636 ACSR and all new 161kV terminal equipment should be rated at 2000A or higher minimum summer normal rating. In addition, a new 161/69kV, 150 MVA transformer will be needed at the Osceola substation. ITC and CIPCO will install new breaker(s) at their respective substations. ITC will be building a new breaker station northeast of the Albia substation. This station will connect the 69kV line from Albia to Court and the 69kV line from Bridgeport to Centerville. Since the two lines have an intersection point (about 1.5 miles NE of the Albia sub), minimal line construction will be needed. ITC will be building a new breaker station at the “Lenox Tap” position. This station will replace the 3-way switch currently in use and connect our Lenox line and substation (IPL owned) to the new 69kV transmission system being built by CIPCO from the northwest (Corning/Brooks). All new 69kV equipment will need to be rated for 1200A minimum summer normal rating. ITC will be installing a 2-way switch outside IPL’s Lenox substation, building a new 69kV line (about 2.6 miles), and connecting it into CIPCO’s substation “Lenox Muni”. ITC will need to coordinate with CIPCO, NEMO, and IPL for necessary outages and construction | IA | IA | 2026-05-01 | Low voltage concerns in southern Iowa. |  |  |  | ITC Midwest | Other | Not Shared | Reliability | 2026-05-01 | 2026-05-01 | 161 | 69 | Planned | 71210187
A in MTEP21 | West | ITCM | 20035 | MPFCA - Hickory Creek and Killdeer 345 kV Cap Bank TO-Funded Network Upgrades | ITC Midwest entered into a Multi-Party Facilities Construction Agreement (“MPFCA”) with MISO and the Interconnection Customers for MISO Projects J302, J476, J503, J512, J555, J569, J583, J587, J590, J611 and J614 for the construction of Network Upgrades at Killdeer 345 kV and Hickory Creek 345 kV. The MPFCA provides for ITC Midwest to fund the cost of 2 x 84 MVAR (rated) capacitor banks at Killdeer 345 kV substation and 2 x 84 MVAR capacitor banks at Hickory Creek 345 kV substation. | IA | IA | 2022-07-01 | ITC Midwest entered into a Multi-Party Facilities Construction Agreement (“MPFCA”) with MISO and the Interconnection Customers for MISO Projects J302, J476, J503, J512, J555, J569, J583, J587, J590, J611 and J614 for the construction of Network Upgrades at Killdeer 345 kV and Hickory Creek 345 kV. |  |  |  | ITC Midwest | GIP |  |  | 2022-07-01 | 2022-07-01 | 345 | 345 | Planned | 16097861
A in MTEP21 | West | ITCM | 20037 | Carbide-Viele 161kV Rebuild | ITC Midwest has entered into an agreement with Northeast Missouri Electric Cooperative to rebuild approximately 12.3 miles of the ITC Carbide – Viele 161 kV line to double circuit to allow Northeast to connect a new 161 kV line from their Franklin Substation in Lee County, Iowa to their Winchester Substation in Clarke County, Missouri. Per the terms of the agreement, Northeast will be responsible for design and construction for this project. ITC will contribute a fixed amount of $6,120,00 for the project as a credit for planned maintenance ITC needs to perform on this line. The ITC portion of the rebuild will be constructed with T2-795 ACSR conductor and OPGW. ITC will own the double circuit poles, conductor, insulators, and 1 OPGW static wire. | IA | IA | 2024-12-31 | Customer requested interconnection. |  |  |  | ITC Midwest | Other |  | Load Growth | 2024-12-31 | 2024-12-31 | 161 | 161 | Planned | 6200000
A in MTEP21 | West | ITCM | 20180 | ITCM Customer Interconnects with short lead time 2024 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | IA,MN,IL | 2024-12-31 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. |  |  |  | ITC Midwest | Other |  | Load Growth | 2024-12-31 | 2024-12-31 | 345 | 69 | Planned | 2400000
A in MTEP21 | West | ITCM | 21429 | Tiffin Crossroads Substation Interconnection | IPL will be building a new 69/25x12.5 kV substation named “Tiffin Crossroads” adjacent to the existing MidAmerican Tiffin Sub K substation. This new substation will replace the existing IPL Tiffin distribution substation and accommodate future area load growth. IPL will be installing one 12/20 MVA transformer initially but is planning the substation to accommodate a 2nd 12/20 MVA transformer in the future. For the ITC owned portion of Tiffin Crossroads, ITC will build a new 69 kV substation with two single boxes, two line breakers, and a bus tie breaker. As part of this, the existing Sub K Tiffin double circuit line tap will be reconfigured to two single circuits, to avoid having a double circuit line tap going into the distribution substation and avoid issues with planned outages on the double circuit requiring the distribution substation to be taken out of service. | IA | IA | 2022-12-31 | Customer requested interconnection |  |  |  | ITC Midwest | Other |  | Load Growth | 2022-12-31 | 2022-12-31 | 69 | 69 | Planned | 5132408
A in MTEP21 | West | ITCM | 21625 | Keokuk Geode 69kV Substation Interconnection | IPL will be building a new 69/25x12.5 kV Substation named Keokuk Geode. The new Keokuk Geode Substation will replace the Messenger Substation and Commercial Substation. IPL will be installing one 69/24.9x12.5 kV 20/33MVA transformer initially but is planning the substation to accommodate a second 69/24.9x12.5 kV transformer when all the load is transferred from the Messenger Substation and Commercial Substation. | IA | IA | 2022-10-30 | Interstate Power and Light Company (IPL) has requested to connect a new substation in Keokuk, IA. |  |  |  | ITC Midwest | Other | Not Shared | Load Growth | 2022-10-30 | 2022-10-30 | 69 | 69 | Planned | 4764418
A in MTEP21 | West | ITCM, MEC | 20685 | J535 Gard Ave. | J535 Network Upgrades and Interconnection Facilities | IA | IA | 2020-04-01 | New three-breaker, 345 kV ring bus substation off the Ida County-Lehigh 345 kV line with two line taps |  |  | This is MEC-ITCM joint owned facility. ITC Midwest owns 28% | MidAmerican Energy Company | GIP |  |  | 2020-04-01 | 2020-04-01 | 345 | 0 | Proposed | 12700000
A in MTEP21 | East | ITCT | 18237 | 2023 ITCT Asset Replacement Program | Replace aging and outdated equipment at a pace that will insure each type of equipment is replaced near its projected end of life. | MI | MI | 2023-12-31 | This Asset Replacement Program will replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use of state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. The Asset Replacement program includes a variety of replacement programs for several types of equipment including but not limited to: • Circuit Breakers/switchers • Protective equipment (relays/control) • DC battery and charging systems • Surge Arresters • Instrument Transformers • Disconnect Switches • Wood poles • Miscellaneous line equipment (insulators, cross-arms, etc.) |  |  |  | ITC Transmission | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 345 | 120 | Proposed | 34200000
A in MTEP21 | East | ITCT | 19185 | Red Run & Bismarck Line Breakers | The proposed solution is to install two 230 kV Line breakers, one at Red Run position “HW” and one at Bismarck position “HC" on the Red Run – Bismarck line. | MI | MI | 2023-12-31 | The Red Run - Bismarck line has a line terminated transformer at Red Run and Bismarck, meaning that primary protection for Red Run T201 protection is dependent on remote clearing at Bismarck through transfer tripping. Similarly, Bismarck T303 protection is dependent on remote clearing of Red Run through transfer tripping. By installing a 230kV line breaker Red Run “HW” and Bismarck “HC” positions, we can provide local tripping for transformer faults. • Relaying - Adds local tripping for the Red Run 230/120 kV Transformer 201 and Bismarck Transformer 303 resulting in: ¿ 25% faster fault clearing. ¿ Increased reliability of transformer protection as primary fault clearing does not rely on power line carrier scheme to trip the remote end breaker. - This improved reliability and reduced fault clearing times can help avoid catastrophic damage for very expensive equipment that have long lead time replacement. • Operations ¿ The installation of the breaker at Red Run would also serve a proper means of dropping line charging current. Without a line breaker at Bismarck the 345kV breakers need to be opened to operate the line. This reduces system reliability by unnecessarily opening the ring bus. • Equipment ¿ There are currently 3 disconnect switches at Red Run that need replacement. Installation of the breaker will eliminate the need to replace 2 of them. ¿ Adding a line breaker at both terminals will make the transformer part of the system. This naturally eliminates any delayed current zero (DCZ) issues. This has the potential of causing the existing breakers to fail when opening a line with an energized transformer. |  |  |  | ITC Transmission | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 230 | 0 | Proposed | 2700000
A in MTEP21 | East | ITCT | 19266 | J799 Interconnection | Construct the J799 Interconnection 120kV station as a three breaker ring bus station. The Milan - Pioneer 120kV line will be extended to loop in the J799 Interconnection station for transmission service. Changes will require relaying upgrades at Milan 120kV | MI | MI | 2022-03-31 | J799 is a 189MW solar generator in the 2017-AUG DPP Cycle. The station is needed to connect J799 to the requested Milan - Pioneer 120kV POI. | None |  |  | ITC Transmission | GIP |  |  | 2022-03-31 | 2022-03-31 | 120 | 0 | M2a_Pre-Project Approval | 7520000
A in MTEP21 | East | ITCT | 19405 | J833 Interconnection | Construct J833 Interconnection station as a breaker and half station with three 40kA breakers in a ring bus configuration. Extend the Milan - Pioneer 120kV line 0.1 miles to loop in J833. | MI | MI | 2022-04-29 | J833 is a 50MW solar plant in the Aug-2017-DPP study cycle. The station is needed to connect the generator. The changes will require updates at Pioneer 120kV to accommodate the new interconnection. | N/A |  |  | ITC Transmission | GIP |  |  | 2022-04-29 | 2022-04-29 | 120 | 0 | M2a_Pre-Project Approval | 10290000
A in MTEP21 | East | ITCT | 19508 | Bauer - Pontiac 345kV Sag Remediation & Station Equipment Upgrade (J701, J794, J796, J832) | Sag remediation requires replacing sixteen (16) 345kV double circuit structures. The terminal equipment upgrade requires replacing four disconnect switches at Pontiac 345kV. | MI | MI | 2021-12-31 | Mitigate thermal violations caused by the J701, J794, J796, and J832 interconnection customers in the August 2017 MISO DPP Phase 3 study. To mitigate the thermal violations ITCT will perform sag remediation on the Bauer - Pontiac 345kV lines as well as replace terminal equipment at Pontiac 345kV. |  |  |  | ITC Transmission | GIP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | M2a_Pre-Project Approval | 8209000
A in MTEP21 | East | ITCT | 19509 | Thetford - Jewell Sag Remediation and Reconductor (J701, J794, J796,J832) | Reconductor approximately 0.1 miles of the Thetford – Jewell 345kV circuit with a conductor rated at least that of 2-945 ACSR. Remediate the sag on the Thetford - Jewell 345kV circuit to achieve a minimum rating of minimum summer emergency circuit rating of 1556 MVA. | MI | MI | 2021-12-31 | Thetford - Jewell is projected to overload due to increase in generation in the area. DPP cycle August 2017 determined generators J701, J794, J796, and J832 contribute to the projected overload. |  |  |  | ITC Transmission | GIP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | M2a_Pre-Project Approval | 5662000
A in MTEP21 | East | ITCT | 19585 | Placid - Pontiac 345kV Sag Remediation (J701,J793,J794,J796,J832) | The scope of this network upgrade involves sag remediation on the Placid - Pontiac 345kV circuit. The sag remediation requires replacing nine 345kV double circuit structures. | MI | MI | 2021-12-31 | The scope of this network upgrade is to mitigate thermal violations caused by the J701, J793, J794, J796, J832, and J839 interconnection customers in the August 2017 MISO DPP Phase 3 study. To mitigate the thermal violations ITCT will raise the sag limit on the Placid - Pontiac 345kV line |  |  |  | ITC Transmission | GIP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | M2a_Pre-Project Approval | 2956000
A in MTEP21 | East | ITCT | 19586 | Pontiac - Wixom 345kV Sag Remediation & Station Equipment Upgrade (J701,J793,J794,J796,J832) | The scope of this network upgrade involves sag remediation on the Pontiac - Wixom 345kV circuit as well as upgrading terminal equipment at Pontiac 345kV & Wixom 345kV. | MI | MI | 2021-12-31 | The scope of this network upgrade is to mitigate thermal violations caused by the J701, J793, J794, J796, J832, and J839 interconnection customers in the August 2017 MISO DPP Phase 3 study. To mitigate the thermal violations ITCT will raise the sag Pontiac - Wixom 345kV line |  |  |  | ITC Transmission | GIP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | M2a_Pre-Project Approval | 2482000
A in MTEP21 | East | ITCT | 19992 | ITCT Pole Top Switch Additions/Replacement Program 2022 | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | MI | MI | 2022-12-31 | Without pole top switches in place, planned or unplanned outages to a transmission line will cause long outages to customers. |  |  |  | ITC Transmission | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 120 | 0 | Proposed | 1000000
A in MTEP21 | East | ITCT | 20036 | Sebewaing 345kV_Installation | Construct New Sebewaing station as a 345kV - 120kV station with three 345kV 40kA breakers and one 120kV 40kA breaker. Install a 345/120kV transformer. Install 4.5 miles of 954 ACSR in new right of way to connect Sebewaing to New ITC Station 120kV at position HQ. Extend the Bauer - Grassmere 345kV line by adding 0.2 miles of 954 ACSR to loop in New ITC Station 345kV for transmission service. | MI | MI | 2024-06-01 | The city of Sebewaing in anticipating a load increase and is seeking to move up to 10MW to the new interconnection. | A 120kV alternative was too expensive as the closest 120kV station is over 12 miles away. |  |  | ITC Transmission | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 345 | 120 | Proposed | 32544000
A in MTEP21 | East | ITCT | 20044 | ITCT Customer Interconnections - Year 2024 | Customer interconnection requests and retirements less than $1 million with in service date in year 2024. | MI | MI | 2024-12-31 | Customer Requests are often in need of interconnection on an expedited basis. This blanket allows interconnection requests of smaller nature to be quickly studied and connected by ITC. |  |  |  | ITC Transmission | Other |  | Load Growth | 2024-12-31 | 2024-12-31 | 120 | 0 | Proposed | 2000000
A in MTEP21 | East | ITCT | 20107 | Atlanta-Karn-Thetford Split & Station Reconfiguration (ITCT) | Install a 120 kV, 3000 Amp, 40 kA section breaker and expand 138 kV into a ring bus configuration Add two 138 kV breakers to configure the 138 kV into a ring bus. Add 0.75 miles of 1431 ACSR to complete the Atlanta – Thetford circuit. New equipment should be rated for 3000 Amps or higher. | MI | MI | 2024-12-31 | Atlanta station is presently configured such that routine NERC required periodic maintenance on some protection systems require the entire station be deenergized for the work to be performed safely. In order to maintain transmission service to the single distribution transformer, a temporary line needs to be constructed to bypass the deenergized Atlanta station. This project will reconfigure the station similar to other ITC stations such that periodic maintenance and other normal work activities can be performed without extensive temporary construction. Adding the section breaker also allows installation of SSVTs to the 120kV buses for station service, allowing for ITC to relocate the backup generator system presently installed. The Atlanta, Karn, and Thetford 138kV line facilities are relayed together; meaning a fault on any one element trips all three and interrupts network transmission flows on the remaining connected elements. The three lines are connect together very near Atlanta station so by bringing the lines the short distance in and out of Atlanta station, we can relay the Karn and Thetford lines individually, which improves system protection as follows: • Less sensitive protection settings on 2-terminal lines, resulting in: ¿ Eliminate risk of overtripping caused by ground miscoordination. ¿ Faster backup clearing times without risk of miscoordination. ¿ Eliminate risk of miscoordination caused by terminals open or with limited infeed. ¿ No concerns with sequential clearing. • The line relaying is newer and will be re-utilized for this 2-terminal line applications with modifications to reduce their complexity to match ITC’s standards: ¿ Increased reliability by reducing risk for human error during operations and maintenance of the schemes. • These 2-terminal lines can utilize double-ended fault locating methods, resulting in the following benefits: ¿ Increased likelihood of locating faults. ¿ Reduce patrol and tower climbing to locate faults. |  |  |  | ITC Transmission | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 138 | 120 | Proposed | 5400000
A in MTEP21 | East | ITCT | 20132 | Pontiac 303 Transformer Replacement | Replace the Pontiac #303 345/120 kV transformer with at least 750 MVA summer emergency rated transformer. | MI | MI | 2025-12-31 | The Pontiac #303 345/120kV transformer is reaching end of life. This transformer is a 1968 General Electric unit that is leaking oil. Electrical testing in 2006 also discovered deteriorated bushings. |  |  |  | ITC Transmission | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 345 | 120 | Proposed | 4800000
A in MTEP21 | East | ITCT | 20133 | Hines 201 Transformer Replacement | Replace the Hines #201 230/120kV transformer. The anticipated replacement is the ITCT-standard 230/120kV 560MVA transformer. | MI | MI | 2025-12-31 | The Hines #201 230/120kV transformer is reaching end of life. This transformer is a 1974 General Electric unit that is leaking oil. |  |  |  | ITC Transmission | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 230 | 120 | Proposed | 4800000
A in MTEP21 | East | ITCT | 20138 | Milan 303 Transformer Replacement | Replace the Milan #303 345/120 kV transformer with at least 750 MVA (3608 Amps) summer emergency rated transformer. | MI | MI | 2023-12-31 | The Milan #303 345/120kV transformer is reaching end of life. This transformer is a 1972 Cogenel unit that was refurbished in 1990. It is leaking oil and was internally producing gasses for a period of time in 2017. |  |  |  | ITC Transmission | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 345 | 120 | Proposed | 4800000
A in MTEP21 | East | ITCT | 20140 | Pontiac 301 Transformer Replacement | Replace the Pontiac #301 345/120kV transformer. The anticipated replacement is the ITCT-standard 345/120kV 560MVA transformer. | MI | MI | 2023-12-31 | The Pontiac #301 345/120kV transformer is reaching end of life. This transformer is a 1968 General Electric unit that is leaking oil. |  |  |  | ITC Transmission | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 345 | 120 | Proposed | 4800000
A in MTEP21 | East | ITCT | 20167 | Cato – Corktown 120 kV | Build approximately 0.85 miles of 120kV 1600mm² underground cable from Cato to Corktown and expand the Cato and Corktown stations to accommodate a third line termination. | MI | MI | 2024-12-31 | Multiple 120 kV underground lines in the Cato and Corktown area with adjacent hazard concerns, involving the need to shutdown lines that are adjacent to other circuits requiring maintenance. This causes the need to deenergize multiple lines in the area leaving one feed at the Cato and Corktown 120 kV stations. |  |  | DTE (load serving entity) has expressed interest in providing the Cato and Corktown 120 kV stations with a third line termination | ITC Transmission | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 120 | 0 | Proposed | 40000000
A in MTEP21 | East | ITCT | 20325 | Custer-Monroe Line Relocation | Relocate approximately 1.8 miles of 120kV circuit at the request of the city of Monroe. | MI | MI | 2022-12-31 | The relocation is required as part of Monroe's upgrades to the River Raisin National Battlefield. |  |  | METC requests this be considered as part of MTEP 2021. | ITC Transmission | Other |  | Other Local Needs | 2022-12-31 | 2022-12-31 | 120 | 0 | Proposed | 8800000
A in MTEP21 | East | ITCT | 20845 | Apache-Seneca 120kV Relocation | Relocate 9 structures of the Apache-Seneca 120kV circuit along Rochester Road in the city of Troy | MI | MI | 2023-12-31 | The city of Troy has directed ITCT to relocate approximately 9 120kV structures along Rochester Road by 12/31/2023. The city has a planned road construction project in which the current structure interfere. |  |  |  | ITC Transmission | Other |  | Other Local Needs | 2023-12-31 | 2023-12-31 | 120 | 0 | Planned | 2040000
A in MTEP21 | East | ITCT | 21026 | Montcalm Equipment Removal and Bypass | Permanently bypass the Montcalm station and remove all ITCT assets. | MI | MI | 2022-12-31 | DTE no longer has any load at the site, and the generation was retired in 2016. |  |  | Either approval in MTEP21 is needed to meet the in service date, requesting pulling forward into MTEP21. There is no change in load or generation associated with the project. | ITC Transmission | Other |  | Other Local Needs | 2022-12-31 | 2022-12-31 | 120 | 0 | Planned | 1640000
A in MTEP21 | East | ITCT | 21047 | Waterman 120kV Reactor HX Replacement | Replace Waterman 120kV series reactor HX with a new series reactor | MI | MI | 2023-12-31 | This reactor has reached it's end of life |  |  |  | ITC Transmission | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 120 | 0 | Proposed | 900000
A in MTEP21 | East | ITCT | 21105 | Apollo Interconnection | Construct a new in-and-out station consisting of a single tie breaker and three straight buses with room for future tie breaker. Install one 120 kV tie breaker, two 120 kV line breakers, buswork, and associated disconnects. Connect two customer owned transformers to the new station. | MI | MI | 2023-05-28 | DTE has requested a new 120 kV interconnection on the ITCT Hunters Creek-Lapeer 120kV circuit. The interconnection request is to feed two DTE transformers, and a future third transformer. |  |  |  | ITC Transmission | Other |  | Load Growth | 2023-05-28 | 2023-05-28 | 120 | 0 | M2a_Pre-Project Approval | 17147252
A in MTEP21 | East | ITCT | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | Henry Ford Macomb Hospital is a DTE interconnection request. ITCT will construct Shrine as a straight bus station with two line breakers and a section breaker. ITCT will extend the Lenox-Stephens 120kV line by adding about 1 mile of 954 DCT to loop in the new station. Fiber will be run from Bismarck 120kV station requiring fiber patches at Bismarck, Jewell, and Sigma 120kV station. Interconnection will require relaying upgrades at Lenox and Stephens. | MI | MI | 2023-06-01 | DTE interconnection for Henry Ford Macomb Hospital. Hospital is expanding, projecting an increase of 2.7 MW of load. Station will serve new load, in addition 3.7 MW of load will be transferred to Shrine from existing DTE distribution stations. |  |  |  | ITC Transmission | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 345 | 0 | M2a_Pre-Project Approval | 14563912
A in MTEP21 | East | ITCT | 21206 | Coventry to Hager 120 kV Projects | Rebuild approximately 1 mile from Duvall tap to Hager utilizing 954 ACSR conductor on standard double circuit steel pole 120 kV structures. Disconnect the 954 ACSR conductor running north from the Baltic Tap and connect it to the 1431 ACSR conductor on the north side of the structures heading toward Coventry 120 kV. Remediate sag from Coventry to the Nitro cut-in to a target rating of 269 MVA SE. Install 3000 A 40 kA 120kV section breaker at Duvall 120 kV and all associated standard 3000 A 40 kA line breakers at Coventry and Hager 120 kV stations | MI | MI | 2023-12-31 | The Sunset – Hager 120kV line is projected to overload for P6 contingencies. |  |  | This is an alternative project to the Hager - Sunset 120 kV Rebuild project (#15959). This alternative mitigates the need to rebuild the Hager - Sunset 120 kV line while providing additional reliability to the loads at the new Nitro 120 kV (project #12443) and the Duvall 120 kV stations. | ITC Transmission | BRP |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Proposed | 10955000
A in MTEP21 | East | ITCT | 21626 | Superior DC Control Relocation | Install a new control building that will be large enough to eventually relocate all the ITCT relaying and controls into it. The new control building will include a dedicated ITCT AC and DC systems large enough to power all ITCTs assets at the substation. All ITCT assets will be cut over to the new dedicated AC/DC system as part of this project. | MI | MI | 2022-12-31 | The existing Superior control building has maintenance, safety, and human performance concerns due to DC reliability issues and the buildings space constraints. The existing DC system feeding the relaying at the station is owned by a third party and has multiple grounds on it. These grounds have caused multiple relay failures during fault events in the vicinity of the station. The older relaying and controls require high operations and maintenance expenses due to their age. The protection panels being dispersed on multiple houses of the creates human performance issues. Additionally, lack of available panel space creates difficulty replacing relaying without extended shutdowns or adding a new dedicated DC system within an existing control house. | Failed Equipment caused by DC Reliability Issues Below are the most concerning past events that were caused by DC reliability issues at Superior. 1. Event: Power Supply failure on carrier and RTU equipment (multiple times). Effect: Potential overtrip concern and loss of station telemetry. 2. Event: Failed RTU equipment (multiple times). Effect: Loss of station telemetry and inability to see breaker statuses. 3. Event: Relays reboot during a fault (multiple relays for the same fault). Effect: Failure to trip 4. Event: DC breakers feeding relays tripped during a fault. Effect: Failure to trip |  |  | ITC Transmission | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 120 | 0 | Proposed | 2000000
A in MTEP21 | West | MDU | 19205 | Tioga Loop | Build a 60 kV loop line around Tioga, ND | ND | ND | 2022-05-31 | Load growth |  |  |  | Montana-Dakota Utilities Company | Other |  | Load Growth | 2021-12-31 | 2021-12-31 | 60 | 0 | Proposed | 1480722
A in MTEP21 | West | MDU | 19605 | Beulah 115/46 kV substation | Replacement of the existing Beulah 115/46 kV substation. | ND | ND | 2022-06-30 | Age & condition of existing Beulah 115 and 46 kV bus and equipment. Improve reliability and operations by replacing old main and transfer bus with a ring bus and replacing old breakers and relays. |  |  |  | Montana-Dakota Utilities Company | Other |  | Age and Condition | 2022-06-30 | 2022-06-30 | 115 | 46 | Planned | 6000000
A in MTEP21 | West | MEC | 2938 | Uprate Sub 39 - Cordova 345 kV Line | Change out a limited number of existing 345 kV line structures to increase rating. | IL | IL | 2022-06-01 | Address Category P6 post-contingent overloads identified in MTEP20 study. |  |  |  | MidAmerican Energy Company | BRP |  |  | 2022-06-01 | 2022-06-01 | 345 | 0 | Planned | 500000
A in MTEP21 | West | MEC | 4247 | Sub 18 - Sub 85 161 KV reconductor | Reconductor the 161 kV line from Sub 85 to Sub 18 and uprate substation terminal equipment | IA,IL | IA | 2022-12-01 | Address congestion observed in MISO real-time operations | None Identifed |  |  | MidAmerican Energy Company | Other | Not Shared | Other Local Needs | 2022-12-31 | 2022-12-31 | 161 | 0 | Proposed | 1600000
A in MTEP21 | West | MEC | 18885 | Clarinda to Braddyville 161 kV Line Rebuild | The project will consist of rebuilding the Clarinda-Braddyville 161 kV line and adding OPGW to improve relaying communication and reduce the potential for misoperations. The line is approximately 12.3 miles. | IA | IA | 2020-10-01 | The Clarinda to Iowa/Missouri state border 161 kV line is one of the oldest 161 kV lines in MidAmerican Energy territory. The wood H-frame line is presently a tie-line with KCPL. KCPL owns the line from Iowa/Missouri state border to Maryville substation in Missouri. The line will be rebuild and OPGW will be added due to its age and condition compared to the rest of the fleet. |  |  |  | MidAmerican Energy Company | Other |  | Age and Condition | 2020-10-01 | 2020-10-01 | 161 | 0 | Planned | 6750000
A in MTEP21 | West | MEC | 18890 | Clarksville-Donald Feldman 69 kV Line | Construct a new 69 kV line between MidAmerican's Clarksville East Substation and Corn Belt Power Cooperative's Donald Feldman Switching Station. | IA | IA | 2020-12-31 | Convert MidAmerican’s Clarksville East-Shell Rock 34.5 kV line to 69 kV. Also, Corn Belt is constructing a new switching station northwest of Shell Rock, Donald Feldman Switching Station; Corn Belt is experiencing rapid load growth in the area. With the additional load, Corn Belt’s 69 kV system needs voltage support during contingencies. Corn Belt has obtained approval from SPP for a 69 kV interconnection between the new Donald Feldman Switching Station and MidAmerican’s Clarksville East Substation. MidAmerican’s Clarksville East-Shell Rock 34.5 kV line is in the vicinity of the new switching station. MidAmerican is pursuing options for a MidAmerican 69 kV line between Clarksville East Substation and the new Donald Feldman Switching Station. |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2020-12-31 | 2021-12-01 | 69 | 0 | Proposed | 5389340
A in MTEP21 | West | MEC | 18891 | Plymouth Substation 161 kV Switches and Jumpers Replacement | Replace seven 161 kV switches and remove one 161 kV switch at Plymouth Substation. Also, replace the jumpers associated with the switches. | IA | IA | 2020-11-01 | Plymouth 161 kV Switches 9460A, 9440B, 9440L, 9610B, 9610L, 9470B, and 9470L are being replaced due to condition. Also, Switch 9460C is being removed and replaced with bus. When the switches are replaced, the jumpers will also be replaced. |  |  |  | MidAmerican Energy Company | Other |  | Age and Condition | 2020-11-01 | 2020-11-01 | 161 | 0 | Planned | 350000
A in MTEP21 | West | MEC | 19745 | 100th & 54th Avenue: Replace 161 kV Breaker 803 | Replace the 161 kV breaker 803 at 100th & 54th Avenue Substation with a breaker that has interrupting rating of 40 kA. | IA | IA | 2022-06-01 | A circuit breaker with a higher fault current interrupting capability will be needed when the second Booneville 345-161 kV transformer is added. |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 161 | 0 | Proposed | 250000
A in MTEP21 | West | MEC | 19994 | Marcus East to Hospers 69 kV Line and Rebuild Marcus East Substation | Construct a new 69 kV line from Hospers-Marcus East, construct new 69 kV line terminal at Hospers Substation, rebuild Marcus East Substation to install 69 kV breakers and a 69 kV capacitor bank | IA | IA |  | Serves new customer load, resolves low voltage that could occur following contingencies by providing a second source into Marcus East Substation |  |  |  | MidAmerican Energy Company | Other |  | Load Growth | 2022-12-01 | 2022-12-01 | 69 | 0 | Proposed | 25400000
A in MTEP21 | West | MEC | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Blanket project to add new 345 kV and 161 kV circuit breakers and replace existing 345 kV, 161 kV and 69 kV circuit breakers to increase reliability and operating flexibility. | IL | IA | 2024-12-31 | Three-year "blanket project" to add new 345 kV and 161 kV circuit breakers and replace existing 345 kV, 161 kV and 69 kV circuit breakers at several existing substations to increase system reliability and operating flexibility. The circuit breaker additions will eliminate existing operating issues such as three-terminal lines. Circuit breakers with operational or failure risk issues such as gassing will be replaced. Specific project locations and scope of work to be determined on an ongoing basis as determined by need. |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2021-12-31 | 2024-12-31 | 345 | 0 | Proposed | 17725000
A in MTEP21 | West | MEC | 19998 | NW 2nd Street Substation | Construct a new 69 kV substation and associated 69 kV line work. | IA | IA |  | Serve new customer load and provide for substation expansion |  |  |  | MidAmerican Energy Company | Other |  | Load Growth | 2022-12-01 | 2022-12-01 | 69 | 0 | Proposed | 10000000
A in MTEP21 | West | MEC | 19999 | Booneville: Second 345-161 kV Xfmr | Add a second 345-161 kV xfmr. Expand 345 kV and 161 kV buses. | IA | IA |  | Serve new customer load. Mitigate thermal overload / curtailment under high wind case. |  |  |  | MidAmerican Energy Company | BRP |  |  | 2023-06-01 | 2023-06-01 | 345 | 161 | Proposed | 16700000
A in MTEP21 | West | MEC | 20000 | Bondurant Substation: Add 345-161 Xfmr | Add a 345-161 kV xfmr. | IA | IA | 2024-12-01 | Mitigate thermal overloads for Category P6 N-1-1 contingencies observed in MTEP20 summer peak models |  |  |  | MidAmerican Energy Company | BRP |  |  | 2024-12-01 | 2024-12-01 | 345 | 161 | Proposed | 11900000
A in MTEP21 | West | MEC | 20002 | Waukee: Add 69 kV Capacitor Bank | Install 69 kV capacitor bank and 69 kV breakers | IA | IA |  | Increase reliability and allow for additional customer load. |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 69 | 0 | Proposed | 1600000
A in MTEP21 | West | MEC | 20003 | Highway 6 161/13.2 kV Substation | Construct a new 161 kV substation and associated 161 kV line work. New substation will have 161 kV connections to Grimes & South Waukee substations from line taps on future 161 kV lines | IA | IA | 2024-12-01 | Serve new customer load |  |  |  | MidAmerican Energy Company | Other |  | Load Growth | 2024-12-01 | 2024-12-01 | 161 | 13.2 | Proposed | 6000000
A in MTEP21 | West | MEC | 20006 | DPS 161 kV Strain Bus Uprate | Uprate strain bus at the Metro East 161 kV line terminal at DPS Substation | IA | IA |  | Mitigates thermal overload in near term summer peak model following P6 N-1-1 contingency event. |  |  |  | MidAmerican Energy Company | BRP |  |  | 2022-06-01 | 2022-06-01 | 161 | 0 | Proposed | 300000
A in MTEP21 | West | MEC | 20007 | Clarion: Add 69 kV Breakers | Presently, Clarion Substation is tapped off the Hampton West--Eagle Grove 69 kV line. Reconfigure the 69 kV lines into Clarion Substation from a single tapped arrangement to an in and out breakered configuration, similar to Goldfield Substation. Build new 69 kV bus on MEC owned property adjacent to existing substation footprint. Install 69 kV circuit switcher between 69 kV bus and existing 69-13 kV transformer. Construct new 69 kV bus to accommodate a future 69 kV bus tie breaker, a future 69 kV circuit switcher, and a future second 69-13 kV transformer. | IA | IA |  | Condition, increase reliability, and serve future load |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2022-03-01 | 2022-03-01 | 69 | 0 | Proposed | 375000
A in MTEP21 | West | MEC | 20008 | Hampton West –Latimer 69 kV Line Uprate | Replacing line structures to obtain maximum conductor rating | IA | IA |  | Increases line rating to accommodate new customer load |  |  |  | MidAmerican Energy Company | Other |  | Load Growth | 2021-06-01 | 2021-06-01 | 69 | 0 | Proposed | 925000
A in MTEP21 | West | MEC | 20010 | Substation 73: 69 kV Line Taps | 69 kV line tap work to support converting Sub 73 from a tapped substation to an in-and-out substation with 69 kV line circuit breakers. | IA | IA |  | Reliability improvement |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 69 | 0 | Proposed | 500000
A in MTEP21 | West | MEC | 20011 | Sub 84: 69 kV Line Taps and Line Upgrades | 69 kV line tap work to support converting Sub 84 from a tapped substation to an in-and-out substation with 69 kV line circuit breakers. Install OPGW from Valley Drive to Sub 84 to Sub 55 for communications and replace structures and conductor on sections of line subject to galloping. | IA | IA | 2023-06-01 | Reliability improvement |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 69 | 0 | Proposed | 5400000
A in MTEP21 | West | MEC | 20012 | Sub 17: Add 161-13.2 kV Transformer | Add 161 kV line circuit breaker at Sub 17 on the Sub 28 line terminal to support the addition of a new 161-13.2 kV transformer. | IA | IA | 2023-06-01 | Serve expanding customer load |  |  |  | MidAmerican Energy Company | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 161 | 0 | Proposed | 1000000
A in MTEP21 | West | MEC | 20013 | Sub 113: 161-69 kV Substation | Add a new 161-69 kV substation bisecting the Oak Grove-Mercer 161 kV line and Sub 108-Sub 111 69 kV line. | IL | IL | 2022-12-31 | Provide a third source to MidAmerican's Sherrard area 69 kV distribution system |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 161 | 69 | Proposed | 5000000
A in MTEP21 | West | MEC | 20038 | Sub 56 - Sub 85 161 kV Line Uprate | Replace substation terminal equipment at Sub 56 to uprate the Sub 56-Sub 85 161 kV line | IA | IA | 2022-12-31 | Address congestion observed in MISO real-time operations |  |  |  | MidAmerican Energy Company | Other |  | Other Local Needs | 2022-12-31 | 2022-12-31 | 161 | 0 | Proposed | 900000
A in MTEP21 | West | MEC | 20121 | Hills 345 kV: Add Two 150 MVAR Capacitors | Expand the Hills 345 kV substation yard from a ring bus to a breaker-and-a-half configuration. Add two 150 MVAR, 345 kV capacitor banks. | IA | IA |  | MISO DPP 2016 August West Network Upgrade. |  |  |  | MidAmerican Energy Company | GIP |  |  | 2022-12-31 | 2022-12-31 | 345 | 0 | Proposed | 12000000
A in MTEP21 | West | MEC | 20123 | Grimes 345 kV Breaker Addition | Add a new 345 kV breaker to the Grimes 345 kV ring bus to eliminate a NERC TPL-001 Category P2 breaker failure contingency | IA | IA |  | MISO DPP 2016 August West Network Upgrade |  |  |  | MidAmerican Energy Company | GIP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | Proposed | 1300000
A in MTEP21 | West | MEC | 20125 | Deep River to Parnell 161 kV Uprate | Replace structures to uprate the rating of the J438 POI Deep River-Parnell 161 kV line | IA | IA |  | MISO DPP 2016 August West Network Upgrade |  |  |  | MidAmerican Energy Company | GIP |  |  | 2020-12-31 | 2020-12-31 | 161 | 0 | Proposed | 225000
A in MTEP21 | West | MEC | 20126 | Braddyville-MO State Line 161 kV Uprate | Reconductor the 161 kV line between the J611 POI Braddyville substation and the Iowa-Missouri border. | IA | IA |  | MISO DPP 2016 August West Network Upgrade |  |  |  | MidAmerican Energy Company | GIP |  |  | 2020-10-01 | 2020-10-01 | 161 | 0 | Proposed | 500000
A in MTEP21 | West | MEC | 20127 | Macksburg-Winterset 161 kV Uprate | Replace structures to uprate the rating of the Macksburg-Winterset 161 kV line | IA | IA |  | MISO DPP 2016 August West Network Upgrade |  |  |  | MidAmerican Energy Company | GIP |  |  | 2020-08-05 | 2020-08-05 | 161 | 0 | Proposed | 120000
A in MTEP21 | West | MEC | 20128 | Montezuma-Diamond Trail 345 kV Uprate | Replace structures to uprate the rating of the Montezuma-J530 POI Diamond Trail 345 kV line | IA | IA |  | MISO DPP 2016 August West Network Upgrade |  |  |  | MidAmerican Energy Company | GIP |  |  | 2020-06-01 | 2020-06-01 | 345 | 0 | Proposed | 250000
A in MTEP21 | West | MEC | 20129 | Diamond Trail-Hills 345 kV Uprate (MISO DPP 2016 Aug.) | Reconductor the J530 POI Diamond Trail-Hills 345 kV Line and uprate Hills substation terminal equipment. | IA | IA |  | MISO DPP 2016 August West Network Upgrade |  |  |  | MidAmerican Energy Company | GIP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | Proposed | 27800000
A in MTEP21 | West | MEC | 20130 | Bondurant-Montezuma 345 kV Uprate (MISO DPP 2016 Aug.) | Replace structures to uprate the rating of the Bondurant-Montezuma 345 kV Line | IA | IA |  | MISO DPP 2016 August West Network Upgrade |  |  |  | MidAmerican Energy Company | GIP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | Proposed | 620000
A in MTEP21 | West | MEC | 20153 | 69 kV Line Rebuilds Blanket 2021 - 2024 | Blanket project to rebuild 69 kV lines due to condition and to improve reliability and operational flexibility. | IA | IA | 2024-12-31 | Three-year "blanket project" to rebuild existing 69 kV lines due to condition. Specific project locations and scope of work to be determined on an ongoing basis as determined by need. |  |  |  | MidAmerican Energy Company | Other |  | Age and Condition | 2021-12-31 | 2024-12-31 | 69 | 0 | Proposed | 27700000
A in MTEP21 | West | MEC | 20154 | 69 kV Substation Line Tap Blanket 2021-2024 | Blanket project to add new 69 kV line taps into new or existing substations to serve new distribution substations or to increase reliability. | IL | IA | 2024-12-31 | Three-year "blanket project" to install 69 kV line taps into several new or existing substations to serve customer loads and/or increase system reliability. Specific project locations and scope of work to be determined on an ongoing basis as determined by need. |  |  |  | MidAmerican Energy Company | Other |  | Load Growth | 2021-12-31 | 2024-12-31 | 69 | 0 | Proposed | 5150000
A in MTEP21 | West | MEC | 20155 | Relaying, Communication and Control Equipment Replacements 2021-2024 | Blanket project to replace existing relaying, communication equipment and control house equipment to increase reliability and operating flexibility. | IL | IA |  | Three-year "blanket project" to replace existing relaying, communication equipment and control house equipment at several existing substations to increase system reliability and operating flexibility. Specific project locations and scope of work to be determined on an ongoing basis as determined by need. |  |  |  | MidAmerican Energy Company | Other |  | Other Local Needs | 2021-12-31 | 2024-12-31 | 345 | 69 | Proposed | 38999000
A in MTEP21 | West | MEC | 20171 | Red Oak-Emerson 69 kV Structure Replacements | Replace structure to obtain the maximum conductor rating at 212F. | IA | IA |  | Reliability improvement |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2022-04-01 | 2022-04-01 | 69 | 0 | Proposed | 200000
A in MTEP21 | West | MEC | 20172 | Percival– Hamburg 69 kV Structure Replacements | Replace structure to obtain the maximum conductor rating at 212F. | IA | IA |  | Reliability improvement |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 69 | 0 | Proposed | 60000
A in MTEP21 | West | MEC | 20173 | Quick-Sub 701 161 kV Line and Line Terminals | Construct a new Quick-Sub 701 161 kV line and line terminals.at Quick and Sub 701. | IA | IA |  | Reliability improvement. Serves existing and expanding customer loads. Provides an additional 161 kV line into the Council Bluffs area. Increases reliability. |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 161 | 0 | Proposed | 17000000
A in MTEP21 | West | MEC | 20175 | Remsen Township Substation & Line Taps | Construct a new substation and 345 kV line taps to accommodate wind farm interconnection (J748) | IA | IA |  | MISO DPP 2017 February Network Upgrade |  |  |  | MidAmerican Energy Company | GIP |  |  | 2021-09-15 | 2021-09-15 | 345 | 0 | Proposed | 13200000
A in MTEP21 | West | MEC | 20176 | Hitchcock 69-13.2 kV Substation | Construct a new 69-13.2 kV distribution substation and associated 69 kV line work | IA | IA | 2022-06-01 | Reliability improvement. This project will allow to retire the existing Honey Creek Substation after being affected by flooding in the area. |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 69 | 0 | Proposed | 3600000
A in MTEP21 | West | MEC | 20177 | Missouri Valley East 69-13.2 kV Substation | Construct a new 69-13.2 kV distribution substation and associated 69 kV line work | IA | IA | 2023-06-01 | Reliability improvement |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 69 | 0 | Proposed | 800000
A in MTEP21 | West | MEC | 20178 | Webster 161 kV Expansion | Expansion of Webster 161 kV to accommodate J524 | IA | IA | 2021-12-01 | MISO DPP 2016 February West Network Upgrade |  |  |  | MidAmerican Energy Company | GIP |  |  | 2021-12-01 | 2021-12-01 | 161 | 0 | Proposed | 3050000
A in MTEP21 | West | MEC | 20189 | Washburn: 161 kV Bus A Improvement | Washburn Bus A: Same upgrades needed on Bus A as are being completed on Bus B under T91PK. The 161 kV circuit switcher on 161-69 kV transformer does not interrupt faults | IA | IA |  | Improve reliability |  |  |  | MidAmerican Energy Company | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 161 | 0 | Proposed | 1002400
A in MTEP21 | West | MEC | 20192 | Rock Valley: Replace 69 kV Breakers & Relays | Replace two 69 kV oil circuit breakers and electromechanical line and bus relaying at Rock Valley Substation | IA | IA |  | Replace due to condition and operational issues |  |  |  | MidAmerican Energy Company | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 0 | Proposed | 1100000
A in MTEP21 | West | MEC | 20626 | Se Soteria Substation & 161 kV Line Taps | New 161 kV distribution substation and associated 161 kV line reconfiguration and construction. | IA | IA | 2022-02-04 | Distribution substation is needed to serve new, large customer load |  |  |  | MidAmerican Energy Company | Other |  | Load Growth | 2022-02-04 | 2022-02-04 | 161 | 13.2 | Proposed | 25300000
A in MTEP21 | West | MEC | 20627 | Johnson Creek Substation & 161 kV Line Taps | New 161 kV distribution substation and associated 161 kV line reconfiguration and construction. | IA | IA | 2022-01-01 | Distribution substation is needed to serve new, large customer load |  |  |  | MidAmerican Energy Company | Other |  | Load Growth | 2022-01-01 | 2022-01-01 | 161 | 13.2 | Proposed | 25300000
A in MTEP21 | West | MEC | 21265 | Sub A Riverside 69 kV Upgrades | Replace 69 kV breakers and protective relaying. Also replace 161-69 kV Transformer Bank 8T1 and 8T2 with a new 161-69 kV, 125 MVA transformer. | IA | IA | 2022-12-31 | MidAmerican plans to install new 69 kV protection and control equipment in this new control house in 2022 to replace the older equipment located in the existing Sub A 69 kV control house. MidAmerican also plans to replace multiple old oil circuit breakers in the Sub A 69 kV yard as part of this project. Existing Sub A 161-69 kV transformers T1 (manufactured in 1947) and T2 (manufactured in 1961) are operated as a single transformer bank and presently utilize 480 VAC auxiliary power sourced from the Riverside Generating Station plant building. This 480 VAC source will no longer be available in 2022. Given the age of the transformers, replacement of transformers T1 and T2 with a single 161-69 kV, 125 MVA transformer similar to the existing Sub A transformer T6 is preferable to converting transformers T1 and T2 to operate on 120/240 VAC auxiliary power. |  |  |  | MidAmerican Energy Company | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 161 | 69 | Planned | 4100000
A in MTEP21 | West | MEC | 21266 | Plymouth 161-69 kV Transformer Replacement | Replace the 161/69 kV (150 MVA) transformer at Plymouth substation which failed recently. The replacement transformer will be a spare 161/69 kV 167 MVA with a load tap changer (LTC). Replace the 13 kV tertiary reactors. | IA | IA | 2021-07-31 | The Plymouth 161-69 kV Transformer AC (150 MVA unit) recently failed and is in the process of being replaced. The replacement transformer will be a spare 161-69 kV, 167 MVA unit with an load tap changer (LTC). Since the replacement transformer has an LTC, the two existing 13 kV reactors connected to the tertiary of the Plymouth transformer will be retired. The new transformer will be purchased to replenish the spare used at Plymouth substation. |  |  |  | MidAmerican Energy Company | Other |  | Age and Condition | 2021-08-31 | 2022-09-30 | 161 | 13 | Planned | 3600000
A in MTEP21 | West | MEC | 21430 | Grimes 345/161 kV Transformer Replacement | Replace 345/161 kV (560 MVA) transformer at Grimes substation which failed recently. The replacement transformer will be a spare 345/161 kV 560 MVA transformer. Retire the 13.8 kV tertiary reactors of the transformer. | IA | IA | 2022-09-30 | The Grimes 345/161 kV transformer recently failed and is in the process of being replaced. The replacement transformer will be a spare 345/161 kV 560 MVA transformer. In addition, one of the 13.8 kV reactors on the tertiary of the failed transformer has a failed RL Switcher and the other 13.8 kV reactor has a failed phase. Given this failed reactor equipment on the tertiary and after reviews by our system control group and planning, we are not replacing the failed reactor equipment when we put the transformer in-service. The equipment will be retired/saved for spares as appropriate, likely later this year. |  |  |  | MidAmerican Energy Company | Other |  | Age and Condition | 2021-07-31 | 2022-09-30 | 345 | 13.8 | Planned | 3850000
A in MTEP21 | West | MEC | 21545 | Diamond Trail to Hills 345 kV Line Structure Replacements | Diamond Trail-Hills 345 kV line structure replacements. | IA | IA | 2022-09-15 | Replace structures based on inspection and condition. |  |  |  | MidAmerican Energy Company | Other | Not Shared | Age and Condition | 2022-09-15 | 2022-09-15 | 345 | 0 | Planned | 3750000
A in MTEP21 | East | METC | 17965 | J806 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Rice Creek - Vrooman 138kV circuit. | MI | MI | 2022-03-31 | J806 is a 149 MW Solar Power Plant that requested to interconnect to the METC Rice Creek - Vrooman 138 kV circuit in the DPP-2017-AUG cycle. |  |  |  | METC | GIP |  |  | 2022-03-31 | 2022-03-31 | 138 | 0 | M3_Long Lead Materials | 12228411
A in MTEP21 | East | METC | 18239 | 2023 METC Asset Replacement Program | Replace aging and outdated equipment at a pace that will insure each type of equipment is replaced near its projected end of life. | MI | MI | 2023-12-31 | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. The Asset Replacement program includes a variety of replacement programs for several types of equipment including but not limited to: • Circuit Breakers/switchers • Protective equipment (relays/control) • DC battery and charging systems • Surge Arresters • Instrument Transformers • Disconnect Switches • Wood poles • Miscellaneous line equipment (insulators, cross-arms, etc.) |  |  |  | METC | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 345 | 138 | Proposed | 36000000
A in MTEP21 | East | METC | 18404 | Nelson Rd - Install 22H9 Breaker | Install a breaker at position 22H9 along with associated disconnect switches to complete row 22 at Nelson Road. | MI | MI | 2022-06-01 | To improve system reliability and mitigate the loss of multiple generating sources into the station due to a breaker fault/failure at 24H9. |  |  |  | METC | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 345 | 0 | Proposed | 1530894
A in MTEP21 | East | METC | 19365 | J806/J857 Stability Mitigation | METC will extend the Marshall – Blackstone 138kV line to loop in J857 Interconnection station. Install two breakers at Stable (the J857 interconnection station) to accommodate the change. | MI | MI | 2022-09-01 | The J806 and J857 interconnections cause stability issues. |  |  |  | METC | GIP |  |  | 2022-09-01 | 2022-09-01 | 138 | 0 | M2a_Pre-Project Approval | 14960000
A in MTEP21 | East | METC | 19385 | J806/J857 Thermal Mitigation | METC will remediate the sag limit on the J806 POI – Denso Jackson 138kV line segment and rebuild approximately 2 miles of the J806 POI – Vrooman 138kV line segment. Replace existing 336 ACSR with 1431 ACSR. | MI | MI | 2022-12-31 | The J806 and J857 interconnections cause thermal overloads. |  |  |  | METC | GIP |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | M2a_Pre-Project Approval | 6308000
A in MTEP21 | East | METC | 19425 | Gleaner - Hackett - Laundra Sag Remediation | Raise the sag limits on the Gleaner - Hackett and Hackett - Laundra line segments of the Bullock - Saginaw River 138kV line. | MI | MI | 2021-12-31 | J794 increases the flow on the Gleaner - Hackett and Hackett - Laundra line segments of the Bullock - Saginaw 138kV line above the sag limit. |  |  |  | METC | GIP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | M2a_Pre-Project Approval | 830000
A in MTEP21 | East | METC | 19445 | Stable - J857 Generator Interconnection | Construct the Stable 138kV as a ring bus station with three 40kA breakers. Loop in the Verona - Foundry 138kV line for transmission service. | MI | MI | 2022-09-01 | J857 is a 124.95 MW solar farm in Calhoun County, MI. |  |  |  | METC | GIP |  |  | 2022-09-01 | 2022-09-01 | 138 | 0 | M2a_Pre-Project Approval | 10853508
A in MTEP21 | East | METC | 19465 | ParrRd-J875-RaisnJ Sag Remediation | Remediate the sag on the Parr Road - J875 Interconnection station and the J875 - Raisin Tap line segment. | MI | MI | 2021-12-31 | J875 is a 150MW solar plant on in the August 2017 DPP study cycle. J875 Generator causes overloads on the line. |  |  |  | METC | GIP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | M2a_Pre-Project Approval | 338400
A in MTEP21 | East | METC | 19506 | Riggsville-Livingston 138kV & Mcgulpin-Riggsville 138kV Dual-Pilot Relay Upgrade (J832) | Install dual pilot relaying on the Riggsville-Livingston 138kV & Mcgulpin-Riggsville lines. The installation of dual pilot relaying on these lines requires installing new relaying and wave traps at Mcgulpin, Riggsville, and Livingston as well as removing breaker bypass switches at Riggsville. | MI | MI | 2022-12-13 | This network upgrade is to improve adverse system stability caused by the J832 interconnection customer in the August 2017 MISO DPP Phase 3 study. |  |  |  | METC | GIP |  |  | 2022-12-13 | 2022-12-13 | 138 | 0 | M2a_Pre-Project Approval | 1487000
A in MTEP21 | East | METC | 19546 | J875 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Parr Road - Whiting 138 kV circuit. | MI | MI | 2022-11-18 | J875 is a 150 MW Solar Power Plant that requested to interconnect to the METC Parr Road - Whiting 138 kV circuit in the DPP-2017-AUG cycle. |  |  |  | METC | GIP |  |  | 2022-11-18 | 2022-11-18 | 138 | 0 | M3_Long Lead Materials | 36523949
A in MTEP21 | East | METC | 19606 | Thetford Station Eq Upgrade, Reconductor, and Sag (J701,J794,J796,J832) | Sag remediation and reconductoring on the Thetford - Jewell 345kV circuit, as well as upgrading station equipment at Thetford 345kV. The sag remediation requires replacing one (1) 345kV double circuit structure. The reconductor requires replacing approximately 325 feet of 2156 ACSR type conductor with 2-954 ACSR type conductor. The terminal equipment upgrade requires upgrading buswork and a line entrance at Thetford. | MI | MI | 2021-12-31 | Mitigate thermal violations caused by the J701, J794, J796, and J832 interconnection customers in the August 2017 MISO DPP Phase 3 study. To mitigate the thermal violations METC will perform sag remediation on the Thetford - Jewell 345kV line as reconductoring and station equipment upgrades. |  |  |  | METC | GIP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | M3_Long Lead Materials | 849000
A in MTEP21 | East | METC | 19625 | Bauer - Pontiac 345kV Sag Remediation (J701,J794,J796,J832) | The scope of this network upgrade involves sag remediation on the Bauer - Pontiac 345kV circuit. The sag remediation requires replacing four (4) 345kV double circuit structures. | MI | MI | 2021-12-31 | The scope of this network upgrade is to mitigate thermal violations caused by the J701, J794, J796, and J832 interconnection customers in the August 2017 MISO DPP Phase 3 study. To mitigate the thermal violations METC will perform sag remediation on the Bauer - Pontiac 345kV line. |  |  |  | METC | GIP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | M3_Long Lead Materials | 1879000
A in MTEP21 | East | METC | 19970 | Rebuild Alma - Vestaburg 138 kV 477 ACSR | Rebuild approximately 0.43 mile of the Alma - Vestaburg 138kV circuit using 954 ACSR on double circuit structures constructed at 138kV Standards with OPGW. Also replace terminal equipment at Alma. | MI | MI | 2024-12-31 | Alma - Vestaburg 138kV line is projected to be overloaded for base case and P1-P7 contingency scenarios during Ludington Pumping and light load conditions. . The identified overloaded equipment on this circuit is the conductor and terminal equipment at Alma. |  |  |  | METC | BRP |  |  | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 2800000
A in MTEP21 | East | METC | 19985 | Murphy 138kV_J1194NU_Install Row12 | Construct Row 12 and install two 63kA breakers at Murphy 138kV. | MI | MI | 2021-11-01 | J1194 is a 224.2 MW wind project in Richland Township, Saginaw county, MI. Generator will connect at position BM12 at Murphy 138kV station. Project is studied in the 2019-DPP-Cycle 1 study cycle. |  |  |  | METC | GIP |  |  | 2021-11-01 | 2021-11-01 | 138 | 0 | M3_Long Lead Materials | 2000250
A in MTEP21 | East | METC | 19991 | METC Pole Top Switch Additions/Replacement Program 2022 | Install or replace an existing a new 138 kV, 2-way, full-load-break pole top switch at various tap points. | MI | MI | 2022-12-31 | Without pole top switches in place, planned or unplanned outages to a transmission line will cause long outages to customers. |  |  |  | METC | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 138 | 0 | Proposed | 2000000
A in MTEP21 | East | METC | 20018 | Rebuild Bullock - Shale 138 kV | Rebuild the Bullock to Structure 006A6682 (approximately 5 miles) utilizing 954 ACSR conductor with 230 kV double circuit structure standards with OPGW. Rebuild from Structure 006A6682 to the future Shale Substation (approximately 15 miles) utilizing 954 ACSR conductor with 138 kV double circuit structures standards with OPGW. Upgrade Terminal equipment at Bullock Substation 188 above overhead line conductor rating. | MI | MI | 2025-06-01 | Bullock to Shale 138 kV line is projected to be overloaded for categories P1, P2, P3, P6, and P7. The overloaded equipment identified on this circuit is the overhead conductor and terminal station equipment at Bullock. |  |  |  | METC | BRP |  |  | 2025-06-01 | 2025-06-01 | 138 | 0 | Proposed | 33000000
A in MTEP21 | East | METC | 20033 | Sag Remediate Weadock - Carter Jct 138 kV | ITC is to remove the sag limit on the 336 ACSR and raise the sag limit on the 636 ACSR to 158F on the Carter - Weadock 138 kV Line. | MI | MI | 2025-06-01 | Carter to Weadock 138 kV line is projected to be overloaded for category P6 contingencies in the peak and shoulder peak cases. |  |  |  | METC | BRP |  |  | 2025-06-01 | 2025-06-01 | 138 | 0 | Proposed | 888000
A in MTEP21 | East | METC | 20047 | METC Customer Interconnections - Year 2024 | Customer interconnection requests and retirements less than $1 million with in service dates in the year 2024. | MI | MI | 2024-12-31 | Customer Requests are often in need of interconnection on an expedited basis. This blanket allows interconnection requests of smaller nature to be quickly studied and connected by METC. |  |  |  | METC | Other |  | Load Growth | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 2000000
A in MTEP21 | East | METC | 20049 | Rebuild and Sag Remediate Gallagher - Twining 138kV | The proposed solution is to Raise the sag limit on the 336 ACSR between Gallagher and Withey Lake Jct. and replace the 1/0 Copper on the Withey Lake Jct. - Twinning 138kV line with 477 ACSR utilizing standard 138 kV double circuit structures | MI | MI | 2025-06-01 | Gallagher to Twining 138 kV line is projected to be overloaded for category P6 contingencies in the light load and off-peak cases. |  |  |  | METC | BRP |  |  | 2025-06-01 | 2025-06-01 | 138 | 0 | Proposed | 971000
A in MTEP21 | East | METC | 20053 | Warren 138 kV 188 Bus Upgrade | Upgrade Warren 188 terminal equipment to meet or exceed the rating of a 954 ACSR conductor. | MI | MI | 2023-12-31 | The Warren – Salt River 138 kV line is projected to be overloaded for category P2, P3, P6, and P7 contingencies in light load and several shoulder peak cases. The overloaded equipment identified on this circuit is the overhead conductor. |  |  |  | METC | BRP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Proposed | 159000
A in MTEP21 | East | METC | 20054 | Warren 138 kV 377 Equipment Upgrades | Upgrade terminal station equipment, including a 138 kV breaker, at Warren position 377 to meet or exceed the rating of a 954 ACSR conductor. | MI | MI | 2023-12-31 | The Warren – Clare Jct. 138 kV line is projected to be overloaded for category P1, P2, P3, and P6 contingencies in light load and several shoulder peak cases. |  |  |  | METC | BRP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Proposed | 1050000
A in MTEP21 | East | METC | 20108 | Atlanta-Karn-Thetford Split & Station Reconfiguration (METC) | Split the three-ended Atlanta-Karn-Thetford 138 kV line into Altanta – Karn 138 kV and Atlanta – Thetford 138 kV. | MI | MI | 2024-12-31 | Atlanta station is presently configured such that routine NERC required periodic maintenance on some protection systems require the entire station be deenergized for the work to be performed safely. In order to maintain transmission service to the single distribution transformer, a temporary line needs to be constructed to bypass the deenergized Atlanta station. This project will reconfigure the station similar to other ITC stations such that periodic maintenance and other normal work activities can be performed without extensive temporary construction. Adding the section breaker also allows installation of SSVTs to the 120kV buses for station service, allowing for ITC to relocate the backup generator system presently installed. The Atlanta, Karn, and Thetford 138kV line facilities are relayed together; meaning a fault on any one element trips all three and interrupts network transmission flows on the remaining connected elements. The three lines are connect together very near Atlanta station so by bringing the lines the short distance in and out of Atlanta station, we can relay the Karn and Thetford lines individually, which improves system protection as follows: • Less sensitive protection settings on 2-terminal lines, resulting in: ¿ Eliminate risk of overtripping caused by ground miscoordination. ¿ Faster backup clearing times without risk of miscoordination. ¿ Eliminate risk of miscoordination caused by terminals open or with limited infeed. ¿ No concerns with sequential clearing. • The line relaying is newer and will be re-utilized for this 2-terminal line applications with modifications to reduce their complexity to match ITC’s standards: ¿ Increased reliability by reducing risk for human error during operations and maintenance of the schemes. • These 2-terminal lines can utilize double-ended fault locating methods, resulting in the following benefits: ¿ Increased likelihood of locating faults. ¿ Reduce patrol and tower climbing to locate faults. |  |  |  | METC | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 322000
A in MTEP21 | East | METC | 20118 | Higgins 138 kV Station Expansion | Reconfigure the Higgins 138 kV station to accommodate the CE request for METC to provide separate and independent exits in the ring bus for 2 new 138/46 kV transformer banks. METC will expand the existing ring bus and install 1 138 kV breaker and associated disconnects. The Mio Dam and Beaver creek lines will be reterminated to improve reliability. | MI | MI | 2023-04-01 | Consumers Energy is rebuilding their 46 kV Higgins station and has requested METC provide separate and independent exits for the new transformer banks. |  |  |  | METC | Other |  | Other Local Needs | 2023-04-01 | 2023-04-01 | 138 | 0 | Proposed | 4490498
A in MTEP21 | East | METC | 20120 | Wackerly 138 kV Station Equipment Upgrades | Replace station equipment in the Wackerly Substation meet or exceed rating of a 795 ACSR conductor. | MI | MI | 2023-12-31 | Equipment at the Wackerly section breaker is projected to be overloaded for category P1, P2, P3, P6 and P7 contingencies in shoulder peak and peak cases. |  |  |  | METC | BRP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Proposed | 142000
A in MTEP21 | East | METC | 20144 | Argenta 2 Transformer Replacement | Replace the Argenta #2 345/138kV transformer. The anticipated replacement is the METC-standard 345/140kV 500MVA transformer. | MI | MI | 2025-12-31 | The Argenta #2 345/138kV transformer is reaching end of life. This transformer is a 1969 Pennsylvania unit that is leaking oil. |  |  |  | METC | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 345 | 138 | Proposed | 5400000
A in MTEP21 | East | METC | 20145 | Tallmadge 2 Transformer Replacement | Replace the Tallmadge #2 345/138kV transformer. The anticipated replacement is the METC-standard 345/140kV 500MVA transformer. | MI | MI | 2025-12-31 | The Tallmadge #2 345/138kV transformer is reaching end of life. This transformer is a 1968 General Electric unit that is leaking nitrogen. |  |  |  | METC | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 345 | 138 | Proposed | 6100000
A in MTEP21 | East | METC | 20146 | Tittabawassee 1 Transformer Replacement | Replace the Tittabawassee #1 345/138kV transformer. | MI | MI | 2023-12-31 | The transformer is reaching its end of life. More details to follow asap. |  |  | A detailed justification document will be uploaded ASAP | METC | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 345 | 138 | Proposed | 6200000
A in MTEP21 | East | METC | 20147 | Vergennes 2 Transformer Replacement | Replace the Vergennes #2 345/138kV transformer. The anticipated replacement is the METC-standard 345/140kV 500MVA transformer. | MI | MI | 2023-12-31 | The Vergennes #2 345/138kV transformer is reaching end of life. This transformer is a 1970 McGraw Edison unit that is leaking oil. Electrical testing in 2009 found that four bushings on this unit have deteriorated as well. |  |  |  | METC | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 345 | 138 | Proposed | 7100000
A in MTEP21 | East | METC | 20162 | Claremont 138 kV Station Rebuild | The proposed solution is to rebuild Claremont 138 kV station with a new control house at a new site just to the southwest of the existing site utilizing new equipment in a five-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called New Station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI | MI | 2025-12-31 | The Claremont 138 kV station is a late 1940’s legacy station. Much of the equipment has been in-service for several decades and has realized the end of its useful life. This equipment is dated (requires the use of operating practices that do not employ the safety measure designed in modern equipment), a source of failure, emergency maintenance, and in need of a wholesale replacement. The station was designed in accordance with design practices of the era. ITC and the industry’s design practices today - utilizing modern high voltage electrical equipment - produces a reliable, safe, accessible, and operationally flexible station. As it stands today, Claremont station’s design and integrity makes it difficult to perform routine maintenance on equipment and presents challenges when conducting routine operations. Furthermore the present station design is such that a single faulted breaker will deenergize the entire station, dropping network load from 7 lines and 2 sub-transmission transformers. |  |  |  | METC | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 24227000
A in MTEP21 | East | METC | 20164 | Wealthy Street 138 kV Station Rebuild | The proposed solution is to rebuild Wealthy Street 138 kV station with a new control house at a new site just to the southwest of the existing site utilizing new equipment in a four-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called New Station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI | MI | 2023-12-31 | The Wealthy Street 138 kV station is an early 1920’s legacy station. Much of the equipment has been in-service for several decades and has realized the end of its useful life. This equipment is dated (requires the use of operating practices that do not employ the safety measure designed in modern equipment), a source of failure, emergency maintenance, and in need of a wholesale replacement. The station was designed in accordance with design practices of the era. ITC and the industry’s design practices today - utilizing modern high voltage electrical equipment - produces a reliable, safe, accessible, and operationally flexible station. As it stands today, Wealthy Street station’s design and integrity makes it difficult to perform routine maintenance on equipment and presents challenges when conducting routine operations. Furthermore the present station design is such that a single faulted breaker will deenergize the entire station, dropping network load from 4 lines and 2 sub-transmission transformers. |  |  |  | METC | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 138 | 0 | Proposed | 24000000
A in MTEP21 | East | METC | 20711 | Stamping Plant 138kV Station Decommission | Terminate 138kV lines and bypass Stamping Plant 138kV station at structure #068C134. Tie Gaines – Stamping Plant to Stamping Plant – Beals Road to create Gaines – Beals Road 138kV line. Decommission Stamping Plant Station and remove all equipment. | MI | MI | 2021-06-01 | The City of Wyoming is requesting ITC to remove the Stamping Plant substation before June 1, 2021. |  |  |  | METC | Other |  | Other Local Needs | 2021-06-01 | 2021-06-01 | 138 | 0 | M5_In Service | 1254000
A in MTEP21 | East | METC | 20826 | Arenac CE Interconnection | Arenac Substation is proposed to connect to the Twining 138kV substation. CE to convey Twining 138kV equipment to METC. METC to provide a new 138kV line between Twining and CE's new Arenac Substation. Fiber will be installed for relay communication. | MI | MI | 2023-01-01 | CE requested a new Interconnection to facilitate the build of a new 138/46kV Arenac Substation for transfer of CE's existing 46kV Twining equipment. |  |  |  | METC | Other |  | Other Local Needs | 2023-01-01 | 2023-01-01 | 138 | 0 | Proposed | 2094931
A in MTEP21 | East | METC | 21025 | Foundry Bypass | Disconnect the Stable - Foundry 138kV line at Calhoun. Disconnect the Foundry - Rice Creek line at structure 074B28. Connect the two lines to make Stable - Rice Creek line. Install one 1-way switch at structure 074B28 for Calhoun. | MI | MI | 2022-09-01 | CE and METC assets are being decommissioned at Foundry 138kV. Foundry should be bypassed as it serves no purpose. The in-service date is needed to minimize costs associated with J857 interconnection. | If in-service date is missed, work will be required at Foundry to support the J857 interconnection. |  |  | METC | Other |  | Other Local Needs | 2022-09-01 | 2022-09-01 | 138 | 0 | M2a_Pre-Project Approval | 1702022
A in MTEP21 | East | METC | 21046 | Livingston 345kV Reactor 34F Replacement | Replace Livingston 345kV Shunt Reactor #34F with a new reactor | MI | MI | 2023-12-31 | This reactor has reached it's end of life. |  |  |  | METC | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 345 | 0 | Proposed | 2500000
A in MTEP21 | East | METC | 21208 | Clinton Station Cut-in | Cut into the Island Rd – Delhi 138 kV line at the Clinton Junction with a new double tap structure and install pole top switches at the Packard and Eaton Rapids taps. Wolverine to utilize existing 795 ACSS conductor on the east side of the structures for the Clinton Rd – Delhi 138 kV circuit and reconductor the line on the west side of the structures utilizing 795 ACSS conductor to complete the Island Rd - Clinton 138 kV circuit | MI | MI | 2025-06-01 | The Delhi – Clinton Jct – Island Rd 138 kV line has experienced several misoperations since Clinton Jct was tapped off the line less than 10 years ago. This is a testament to the complexity of three-terminal line relaying. Furthermore, this scheme is so sensitive that it’s picking up and blocking routinely for faults as far away as Fermi. As the carrier equipment degrades over time, we should expect additional misoperations if actions are not taken. • Less sensitive protection settings on 2-terminal lines, resulting in: ¿ Eliminate risk of overtripping caused by ground miscoordination. ¿ Faster backup clearing times without risk of miscoordination. ¿ Eliminate risk of miscoordination caused by terminals open or with limited infeed. ¿ No concerns with sequential clearing. • The line relaying is newer and may be re-utilized for this 2-terminal line applications with modifications to reduce their complexity to match ITC’s standards: ¿ Increased reliability by reducing risk for human error during operations and maintenance of the schemes. • These 2-terminal lines can utilize double-ended fault locating methods, resulting in the following benefits: ¿ Increased likelihood of locating faults. ¿ Reduce patrol and tower climbing to locate faults. ¿ Quicker restoration. | Along with the protection issues this project mitigates, this alternative also provides long term benefits per Wolverine’s “Clinton Area Alternative” project entry (#21205) |  |  | METC | Other |  | Reliability | 2025-06-01 | 2025-06-01 | 138 | 0 | Proposed | 3300000
A in MTEP21 | East | METC | 21305 | North Belding - Control House Replacement | Install new Control House at North Belding 138kV station. Migrate relaying and vacate old control houses. Install SSVTs and Battery system. | MI | MI | 2024-06-01 | Mitigate working space constraints and multiple control houses that can lead to human performance related issues during switching and cutting out protection. Replacement of remaining electromechanical relay schemes to microprocessor relays. |  |  |  | METC | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 138 | 0 | Proposed | 1960830
A in MTEP21 | West | MP | 18066 | Badoura 115kV Substation Modernization | Relocate existing 115 kV lines into ring bus and remove/retire old substation yard. | MN | MN | 2023-12-31 | Age & condition |  |  |  | Minnesota Power (Allete, Inc.) | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 115 | 0 | Proposed | 1820000
A in MTEP21 | West | MP | 18945 | 98 Line Asset Renewal | Structure replacements on Iron Range - Arrowhead 230 kV line | MN | MN | 2021-03-31 | Age & condition |  |  |  | Minnesota Power (Allete, Inc.) | Other |  | Age and Condition | 2021-03-31 | 2021-03-31 | 230 | 0 | Planned | 2130000
A in MTEP21 | West | MP | 20032 | Canosia Road Substation Expansion | Complete ring bus and add 115/34.5 kV transformer to existing Canosia Road Substation. This project includes the transmission equipment necessary to accommodate the new transformer. | MN | MN | 2022-12-31 | Redundancy and load-serving capability for Cloquet area. |  |  |  | Minnesota Power (Allete, Inc.) | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 115 | 34.5 | Proposed | 1500000
A in MTEP21 | West | MP | 20075 | Forbes 230 kV Modernization | Replace aging 230 kV cap bank and 230 kV circuit breakers at Forbes Substation, as well as a large 230/115 kV autotransformer. Project includes several other asset renewal components and substantial civil work at the site. | MN | MN | 2025-12-31 | Asset Renewal |  |  |  | Minnesota Power (Allete, Inc.) | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 230 | 0 | Proposed | 7350000
A in MTEP21 | West | MP | 20081 | Stinson Asset Renewal Project | Replace aging capacitor bank, 115W breaker, switches, PT's, and relay panels. | WI | WI | 2022-12-31 | Asset renewal. |  |  |  | Minnesota Power (Allete, Inc.) | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 115 | 0 | Proposed | 1530000
A in MTEP21 | West | MRES | 19845 | Willmar South Breaker Replacement | Replace oil filled breakers due to age and condition | MN | MN | 2021-12-31 | Breaker replacement |  |  |  | Missouri River Energy Services (MRET) | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 0 | M4_Pre-Construction | 800000
A in MTEP21 | West | MRES | 19846 | Willmar Plant Sub Relocate | The Willmar Power Plant building is being decommissioned and removed. Substation protection and controls were in the building and will need to be moved. This will require the entire substation to be moved to a new location. | MN | MN | 2021-12-31 | New substation location for the Willmar Plant Substation. |  |  |  | Missouri River Energy Services (MRET) | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 69 | 0 | Planned | 3000000
A in MTEP21 | West | MRES | 19986 | Willmar Sub Upgrades | Upgrading bus jumpers, switches, and oil filled breakers at the Willmar 230/69 kV substation. | MN | MN | 2022-12-30 | Age and condition of equipment |  |  |  | Missouri River Energy Services (MRET) | Other |  | Age and Condition | 2022-12-30 | 2022-12-30 | 230 | 69 | Planned | 610000
A in MTEP21 | West | MRES | 20445 | Atlantic Breaker Replacement | Replace 69 kV oil breaker at NIPCO J8 substation. | IA | IA | 2021-12-31 | Breaker replacement age and condition. |  |  |  | Missouri River Energy Services (MRET) | Other | Not Shared | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 0 | Under Construction | 100000
A in MTEP21 | Central | NIPS | 20112 | Rebuild Fair Oaks 138/69 kV Substation | Install new 138/69/12 switchable 22.4 MVA transformer. Install a new 69 kV line terminal with auto throwover scheme equipment for a new loop line to Colfax. Expand the fence and install new 69 kV rigid bus. | IN | IN | 2021-04-30 | Increased load requires more capability. Loop for reliability to area. |  |  |  | Wabash Valley Power Association, Inc. | Other |  | Age and Condition | 2021-04-30 | 2021-04-30 | 69 | 12 | Planned | 4700000
A in MTEP21 | Central | NIPS | 20113 | Update Colfax South Substation | Install a new 69 kV line terminal with an auto sectionalizing scheme equipment for a new loop line to Fair Oaks. | IN | IN | 2021-12-31 | Reliability to area |  |  |  | Wabash Valley Power Association, Inc. | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 12 | Planned | 1500000
A in MTEP21 | Central | NIPS | 20114 | New 69kV Fair Oaks to Colfax South | New 138kV (Operated at 69 kV) 477 ACSR conductor looping Colfax to Fair Oaks for reliability in Jasper and Newton Counties. | IN | IN | 2021-12-31 | Reliability in Jasper and Newton Counties |  |  |  | Wabash Valley Power Association, Inc. | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 69 | 12 | Planned | 5300000
A in MTEP21 | Central | NIPS | 20605 | Rebuild Michigan City (Shoreline) 138 kV Substation | Rebuild of Michigan City 138kV substation. | IN | IN | 2022-12-31 | Age & Condition |  |  |  | Northern Indiana Public Service Company | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 138 | 0 | Planned | 16572178
A in MTEP21 | West | OTP | 16286 | Donaldson-Hallock 41.6 kV Line Upgrades | Repole and reinsulate 8.8 miles to a 69 kV level on the transmission line between Donaldson-Hallock 41.6 kV for reliability. | MN | MN | 2020-12-15 | Age and condition of 8.8 miles between Donaldson to Hallock 41.6 kV transmission line will be repoled and reinsulated to a 69 kV level. |  |  | 1-15-2020 ISD changed from 3/31/2021 to 12/15/2020. 7-15-2020 MISO Please change to Appendix A from Appendix B. Change Requested Cycle MTEP19 to MTEP21. Please notice ISD changed from 12/30/2021 to 3/31/2021. | Otter Tail Power Company | Other |  | Age and Condition | 2020-12-15 | 2020-12-15 | 41.6 | 0 | M5_In Service | 1400483.7
A in MTEP21 | West | OTP | 19929 | OTP Finley to McVille 41.6 kV Line Upgrade | Rebuild 5.75 miles of 41.6 kV line and add automation to existing switches to improve reliability performance and restoration time of this line. | ND | ND | 2021-12-01 | Structure integrity of existing line is leading to reliability concerns |  |  |  | Otter Tail Power Company | Other |  | Age and Condition | 2021-12-01 | 2021-12-01 | 41.6 | 0 | Planned | 1000000
A in MTEP21 | West | OTP | 19930 | OTP Doyon/Bartlett – Rebuild 41.6 kV Line | Rebuild 5.6 miles of 41.6 kV line, replace conductor and reroute existing line out of the water to improve reliability performance and restoration time of this line. | ND | ND | 2021-12-01 | Structure integrity of existing line is leading to reliability concerns. |  |  |  | Otter Tail Power Company | Other |  | Age and Condition | 2021-12-01 | 2021-12-01 | 41.6 | 0 | Planned | 950000
A in MTEP21 | West | OTP | 20485 | OTP Ortonville 115 kV Capacitor Reduction | Reduce capacitor size from 30 MVAR to 17 MVAR. | MN | MN | 2020-09-24 | The existing capacitor was too large and voltage jumps exceeded OTP switching criteria. The lower size keeps the voltage jumps within OTP criteria. |  |  |  | Otter Tail Power Company | Other |  | Reliability | 2020-09-24 | 2020-09-24 | 115 | 0 | M5_In Service | 1000
A in MTEP21 | West | OTP | 20606 | OTP Maple River 345/230/13.8 kV Transformer Replacement | Like-for-like replacement of the failed Maple River 345/230/13.8 kV transformer #1. Additionally, a new control house will be built. | ND | ND | 2022-02-04 | One of OTP’s transformers failed at Maple River, so a replacement is required. |  |  | 9/10/2021 ISD changed from 12/31/2021 to 2/4/2022 1/14/2021 ISD changed from 10/29/2022 to 12/31/2021 | Otter Tail Power Company | Other |  | Age and Condition | 2022-02-04 | 2022-02-04 | 345 | 230 | Planned | 2600000
A in MTEP21 | Central | PPI | 19847 | New Golden 138/69 kV Substation | New Golden 138/69 kV substation near La Prairie, IL | IL | IL | 2024-12-31 | Provide alternative feed to Adams Electric Cooperative and backup St. Anthony transformer. |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 138 | 69 | Planned | 7425000
A in MTEP21 | Central | PPI | 19848 | New Camden - Rushville 69 kV Line | New ~12-mile Camden to Rushville 69 kV line in AEC | IL | IL | 2024-12-31 | Provide alternative feeds to Camden and Rushville substations |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 7680000
A in MTEP21 | Central | PPI | 19849 | New Rushville - Sugar Grove 69 kV Line | New ~13-mile Rushville to Sugar Grove 69 kV line in AEC | IL | IL | 2024-12-31 | Provide alternative feeds to Rushville and Sugar Grove substations |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 8448000
A in MTEP21 | Central | PPI | 19850 | New Sugar Grove - Mt. Sterling 69 kV Line | New ~9-mile Sugar Grove to Mt. Sterling 69 kV line in AEC | IL | IL | 2024-12-31 | Provide alternative feeds for Sugar Grove and Mt. Sterling substations |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 5548800
A in MTEP21 | Central | PPI | 19851 | New Mt. Sterling - Kellerville 69 kV Line | New ~18-mile Mt. Sterling to Kellerville 69 kV line in AEC | IL | IL | 2024-12-31 | Provide alternative feeds to Mt. Sterling and Kellerville substations |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 0 | Planned | 11328000
A in MTEP21 | Central | PPI | 19932 | New Disco to Lomax 69 kV Line | New ~15-mile Disco to Lomax 69 kV line in WIEC | IL | IL | 2024-12-31 | Provide alternative feeds to Disco and Lomax substations |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 9862500
A in MTEP21 | Central | PPI | 19933 | New Disco to Powellton 69 kV Line | New ~12-mile Disco to Powellton 69 kV line in WIEC | IL | IL | 2024-12-31 | Provide alternative feeds to Disco and Powellton substations |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 8000000
A in MTEP21 | Central | PPI | 19934 | Add Elvaston 69 kV Breakers | Add breakers on the Elvaston to Powellton line and the Elvaston to Sutter line | IL | IL | 2024-12-31 | Provide protection for the Elvaston to Powellton line and Elvaston to Sutter line |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 350000
A in MTEP21 | Central | PPI | 19935 | New Sutter - Ursa 69 kV Line | New ~21-mile Sutter to Ursa 69 kV line between WIEC and AEC | IL | IL | 2025-12-05 | Provide alternative feeds to Sutter and Ursa substations |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 69 | 0 | Planned | 13312000
A in MTEP21 | Central | PPI | 19937 | New Bluffs 69 kV Breaker Substation | New Bluffs 69 kV Breaker substation located near Bluffs, IL in IEC | IL | IL | 2023-12-31 | Provide sectionalizing for Bluffs to Winchester, Bluffs to Naples, and Bluffs to Indian Creek 69 kV lines. |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 69 | 69 | Planned | 2844450
A in MTEP21 | Central | PPI | 19938 | Rebuild Grand Island - Poplar City 69 kV Line | Rebuild ~1-mile Grand Island to Poplar City 69 kV line in MEC | IL | IL | 2021-12-31 | Age and Condition. Replace 2/0 line built in 1955 with 556.5 MCM ASCR conductor |  |  |  | Prairie Power, Inc. | Other |  | Age and Condition | 2020-12-31 | 2020-12-31 | 69 | 69 | M5_In Service | 557290
A in MTEP21 | Central | PPI | 19939 | Rebuild Grand Island - Topeka 69 kV Line | Rebuild ~5-mile Grand Island to Topeka 69 kV line in MEC | IL | IL | 2021-12-31 | Age and Condition. Replace 2/0 line built in 1955 with 556.5 MCM ASCR conductor |  |  |  | Prairie Power, Inc. | Other |  | Age and Condition | 2022-05-31 | 2022-05-31 | 69 | 69 | Planned | 2407310
A in MTEP21 | Central | PPI | 19940 | Replace Grand Island 138/69 kV Transformer | Replace 56 MVA Delta-Wye 138/69 kV transformer with 84 MVA Wye-Wye 138/69 kV transformer | IL | IL | 2024-12-31 | Allow Grand Island transformer to phase with and backup Indian Creek and Fancy Creek transformers |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 138 | 69 | Planned | 1500000
A in MTEP21 | Central | PPI | 19949 | New ISHI Shelbyville 69 kV Loop | New ~7-mile ISHI Distribution to Johnston to Crest to Airport 69 kV line in SEC | IL | IL | 2025-12-31 | Provide alternative feeds to ISHI Distribution, Johnston, Crest, and Airport substations |  |  |  | Prairie Power, Inc. | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 69 | 69 | Planned | 4064000
A in MTEP21 | Central | PPI | 19951 | Rebuild Pisgah Tap - Berlin 69 kV Line | Rebuild Pisgah Tap to Berlin 69 kV line between IEC and MEC | IL | IL | 2021-12-31 | Age and Condition. Replace 4/0 line built in 1965 with 336.4 MCM ASCR conductor |  |  |  | Prairie Power, Inc. | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 69 | 69 | Planned | 7880000
A in MTEP21 | Central | PPI | 20607 | New Illinois Winds Pittsfield 69 kV Generator Interconnection | New Illinois Wind Panther Creek 44.5 MW Wind Farm connecting to the PPI Pittsfield 69 kV bus. | IL | IL | 2023-01-31 | Connect Illinois Winds Panther Creek 44.5 MW Wind Farm to PPI Pittsfield 69 kV bus. Based on the projected 1/31/2023 in-service date, PPI is requesting that this generator interconnection project be placed in MTEP21 |  |  | At the request of MISO this project did not go through the MISO queue. Instead, PPI and its consultant, GDS Associates, performed the appropriate studies and PPI secured the Generation Interconnection Agreement with Illinois Winds. | Prairie Power, Inc. | GIP | Not Shared |  | 2023-01-31 | 2023-01-31 | 69 | 0 | Proposed | 6676401
A in MTEP21 | South | SMEPA | 20305 | MS Solar 4 Switching Station | Construct a new 161kV breaker switching station that taps the Moselle - Columbia 161kV line. | MS | MS | 2022-10-01 | The new 161kV breaker switching station is required as the POI for Interconnection Customer project J1144 (MS Solar 4). |  |  |  | South Mississippi Electric Power Association | GIP |  |  | 2022-10-01 | 2022-10-01 | 161 | 0 | Planned | 5251585
A in MTEP21 | East | WPSC | 20885 | Cimmaron Interconnection | Install tap pole and 2 switches on White Cloud to Hesperia line section to allow Consumers to interconnect service for new Cimmaron substation. | MI | MI | 2022-12-31 | New Load Interconnection |  |  |  | Wolverine Power Supply Cooperative, Inc. | Other |  | Load Growth | 2022-12-31 | 2022-12-31 | 69 | 0 | Proposed | 600000
A in MTEP21 | East | WPSC | 21205 | Clinton Area Alternative | Wolverine proposes to utilize Wolverine’s existing Clinton station and double circuit line as an alternative to METC’s MTEP Project #20158. In order to address other future drivers, Wolverine also proposes to convert its Bradley to Clinton line from 69kV to 138kV that is additional to METC’s protection needs. See Exhibit 1 for one-line diagram of configuration (Warning – CEII information) The scope of work includes: • Reconfiguring Wolverine’s Clinton Station to create an in-and-out path for METC’s Delhi – Island Road 138kV line and accommodate the converted Bradley– Clinton 138kV line • Replacing 4/0 conductor on one circuit of Clinton’s double circuit line with 795ACSS • Replacing the Vermontville high side to accommodate 138kV operation • Replacing the Hastings high side to accommodate 138kV operation • Replacing the Otsego high side to accommodate 138kV operation • Rebuilding Wolverine’s Eaton Rapids 69 kV line to 138 kV design and relocating from Clinton Station to METC’s Delhi-Island Road line. • Replacing the Eaton Rapids high side to accommodate 138kV operation | MI | MI |  | The southeastern area of Wolverine’s transmission system is in need of several upgrades driven by both reliability and condition. Each driver is disconnected from each other but when put together creates a holistic solution that mitigates the needs for all. Reliability 1. Support METC’s need for improved protection coordination on the Delhi – Island Road 138kV 2. Address the inefficiencies from recurring 69kV to 138kV backflow at Clinton (see Exhibit 2 for 2019 and 2020 flow data) 3. Mitigate voltage constraints under long-term forecasts (10-15 years) Condition 1. Rebuild of the Eaton Rapids line will soon be required due to condition • Current age 67 years, built in 1953 • 7 condemned, 36 damaged poles • 25% of poles in need of replacement |  |  |  | Wolverine Power Supply Cooperative, Inc. | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 13650000
A in MTEP21 | West | XEL | 19165 | Fieldon Retirement | This project bypasses and retires the Fieldon series capacitor and removes the substation, whose only function is for the series capacitor. This facility is no longer required and has a significant recurring maintenance cost. | MN | MN | 2022-07-01 | The system growth in the area has removed the need for the Fieldon series capacitor which has had operational issues in the past and has a significant recurring maintenance cost. |  |  |  | Northern States Power (Xcel Energy) | Other |  | Age and Condition | 2022-07-01 | 2022-07-01 | 345 | 0 | Proposed | 3000000
A in MTEP21 | West | XEL | 19886 | Minnesota Vallery TR12 ELR | Like for like replacement of Minnesota Valley TR12. Transformer is 68 years old and is experiencing performance issues | MN | MN | 2021-12-15 | Transformer is 68 years old and has indications of some overheating issues, moisture, bad joints, and active thermal degradation. Not replacing would result in more frequent and long term outages. |  |  |  | Northern States Power (Xcel Energy) | Other |  | Age and Condition | 2021-12-15 | 2021-12-15 | 115 | 69 | Planned | 1500000
A in MTEP21 | West | XEL | 19887 | Eau Claire TR10 ELR | End of life, like for like replacement of Eau Claire TR10. | WI | WI | 2021-12-15 | Eau Claire TR10 is 52 years old and is experiencing performance issues. Potential for more frequent and longer duration outages. |  |  |  | Northern States Power (Xcel Energy) | Other |  | Age and Condition | 2021-12-15 | 2021-12-15 | 345 | 161 | Planned | 3000000
A in MTEP21 | West | XEL | 19888 | Northfield to Farmington Line Rebuild | Rebuild approximately 18.6 miles of existing Northfield to Farmington line to current Transmission Design Standards. Reconductor 1.3 miles | MN | MN | 2022-12-15 | End of life,at risk of imminent failures. Increased outage frequency and duration. Failure could provide risk to public safety |  |  |  | Northern States Power (Xcel Energy) | Other |  | Age and Condition | 2022-12-15 | 2022-12-15 | 69 | 0 | Proposed | 8000000
A in MTEP21 | West | XEL | 19889 | Black Oak to Sauk Center Line Rebuild | Rebuild and upgrade conductor on approximately 6.64 miles from Black Oak to Sauk Center. | MN | MN | 2024-06-01 | Structures exceed planned service life - built in 1951. 4/OA and 3/#6 CU line sections overloading on N-1 contingencies. |  |  |  | Northern States Power (Xcel Energy) | Other |  | Reliability | 2024-06-01 | 2024-06-01 | 69 | 0 | Proposed | 4000000
A in MTEP21 | West | XEL | 19890 | Watkins - Kimball Line Rebuild | Rebuild and upgrade approximately 6.56 miles of existing line. Replace EOL switches and MODs. | MN | MN | 2022-12-15 | 83 year old poles. Age and condition do not support repairs. Load growth requires upgrade of small conductor. Potential for increased outage frequency and duration. Failure could provide risk to public |  |  |  | Northern States Power (Xcel Energy) | Other |  | Load Growth | 2022-12-15 | 2022-12-15 | 69 | 0 | Proposed | 3200000
A in MTEP21 | West | XEL | 19891 | Replace Green Isle Substation | Replace existing Green Isle substation with a new 69/13.8 kV substation on a new site. | MN | MN | 2021-03-15 | Addition of industrial load is planned. Existing TR1 has contingency risk post load addition. Existing substation is 4kV and needs to be converted to conform with standards, existing site not sized to fit |  |  |  | Northern States Power (Xcel Energy) | Other |  | Load Growth | 2021-03-15 | 2021-03-15 | 69 | 13.8 | Planned | 3500000
A in MTEP21 | West | XEL | 19892 | Elm Creek TR4 | Install Elm Creek TR4 at 115kV/34.5kV with one new 34.5kV feeders exiting the substation to remediate N-1 overloads and allow proposed new customer load | MN | MN | 2021-12-15 | Extended outage duration under Transformer N-1 contingency to mitigate overloads. New customer load interconnecting to substation. |  |  |  | Northern States Power (Xcel Energy) | Other |  | Load Growth | 2021-12-15 | 2021-12-15 | 115 | 34.5 | Planned | 4070000
A in MTEP21 | West | XEL | 19893 | Great Plains Substation | Construct new 115kV substation in Sioux Falls, SD between West Sioux Falls - Cherry Creek 115kV; 4 rows breaker-and-a-half; 3 TRs, 4 lines, 115 kV cap. | SD | SD | 2022-10-15 | Additional capacity needed to continue reliably serving customers in the Southwest area of Sioux Falls. Remediates N-1 distribution risk. |  |  |  | Northern States Power (Xcel Energy) | Other |  | Reliability | 2022-10-15 | 2022-10-15 | 115 | 13.8 | Planned | 10600000
A in MTEP21 | West | XEL | 19905 | 2589 - Barnes Grove Interconnection | Install 3-way switch on 69kV line between Inver Grove - Keagan Lake Tap to accommodate GRE’s new Barnes Grove interconnection (MTEP 2589) | MN | MN | 2021-04-14 | GRE interconnecting new Barnes Grove substation to serve new customer load |  |  |  | Northern States Power (Xcel Energy) | Other |  | Load Growth | 2021-04-14 | 2021-04-14 | 69 | 0 | Planned | 350000
A in MTEP21 | West | XEL | 19906 | Prentice Cap Bank Replacement | Upgrade the cap bank to 10MVAR and replace the circuit switcher at Prentice substation. | WI | WI | 2021-12-15 | Reliability concerns with aging Cap Bank experiencing multiple failures over the years and circuit switcher not rated for -50 deg. C. |  |  |  | Northern States Power (Xcel Energy) | Other |  | Reliability | 2021-12-15 | 2021-12-15 | 115 | 0 | Planned | 1000000
A in MTEP21 | West | XEL | 19913 | Howard Lake to Big Swan, Delano to Howard Lake, Cokato to Winstead Rebuild | Howard Lake to Big Swan - Rebuild 16.0 miles , Delano to Howard Lake – Rebuild 19.7 miles , Cokato to Winstead – Rebuild 14.3 miles to current 69kV standard for end of life asset renewal | MN | MN | 2024-06-15 | Re-occurring system reliability issues increase, Public safety concerns Inability to serve load in long term |  |  |  | Northern States Power (Xcel Energy) | Other |  | Reliability | 2024-06-15 | 2024-06-15 | 69 | 0 | Planned | 28000000
A in MTEP21 | West | XEL | 19914 | High Bridge-Rogers Lake Bifurcation to Double Circuit | Convert the bifurcated 115 kV line from High Bridge to Rogers Lake to a double circuit 115 kV line to alleviate curtailment on the High Bridge Generating Plant. Construct new breaker positions at High Bridge and Rogers Lake to accommodate the second 115kV circuit | MN | MN | 2023-05-01 | Relieve congestion issues historically seen at the High Bridge 115kV substation |  |  |  | Northern States Power (Xcel Energy) | Other |  | Reliability | 2023-05-01 | 2023-05-01 | 115 | 0 | Planned | 3420000
A in MTEP21 | West | XEL | 19915 | Replace Alma Substation | Replace the existing Alma sub which is at end of life and in a poor access location with new sub with 7MVA TR with two regulated feeders at new site. | WI | WI |  | The existing Alma substation is at end of life with 72 year old transformers. Access, space, and clearances are inadequate to rebuild in place |  |  |  | Northern States Power (Xcel Energy) | Other |  | Age and Condition | 2022-10-15 | 2022-10-15 | 69 | 12.5 | Planned | 3000000
A in MTEP21 | West | XEL | 19916 | Rebuild Genoa Substation | Rebuild Genoa sub which is at end of life with New sub with 7MVA TR with two feeders on the existing site. | WI | WI | 2022-10-15 | Genoa has reached end of life. Failing equipment has caused several long outages. |  |  |  | Northern States Power (Xcel Energy) | Other |  | Age and Condition | 2022-10-15 | 2022-10-15 | 69 | 13.8 | Planned | 2700000
A in MTEP21 | West | XEL | 20135 | Panther - Big Swan Rebuild | - Rebuilding most of the line to 477 standard due to age and condition - Adding a breaker station at Adams Wind tap to sectionalize the line - Converting the City of Litchfield tap structure to a double circuit structure | MN | MN | 2024-12-31 | Rebuilding line for age and condition and to support addition of Adams Wind |  |  |  | Northern States Power (Xcel Energy) | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 0 | Planned | 33300000
A in MTEP21 | West | XEL | 20229 | J732 Stone Lake XFMR Upgrade | Transformer upgrade for J732 in Aug 17 ATC DPP cycle | WI | WI | 2023-11-10 | Transformer overload with addition of J732 |  |  |  | Northern States Power (Xcel Energy) | GIP |  |  | 2023-11-10 | 2023-11-10 | 345 | 161 | Planned | 3600000

## Fac Legend
MTEP Database Export
Facility Table Field Legend
Project table has blue highlighted header. A project may have multiple facilties.
Facility table has beige highlighted header. A project's facilities may have different in service dates.
Facilty Table Field Legend
Field | Description
Target Appendix | Target appendix for the MTEPyy planning cycle. Example: "A in MTEP15" projects were reviewed in MTEP15.
Region | MISO Planning Region: Central, East, West or South
Geographic Location by TO Member System | Project geographic location by Transmission Owner member systems
PrjID | Indicates the Facility's Project. Projects may have multiple facilities.
Facility ID | Facility ID: MISO facility identifier
Expected ISD | Expected In Service Date for this facility
From Sub | From substation for transmission line or location of transformer or other equipment
To Sub | To substation for transmission line or transformer designation
Ckt | Circuit identifier
Max kV | Maximum voltage of this facility
Min kV | Minumum voltage of this facility (transformer low-side voltage)
Facility Rating | Rating of the facility in applicable units. Typically Summer rate
Facility Description | Brief description of transmission facility
State | State the facility is located in
Miles Upg. | Transmission line miles on existing rights of way (ROW)
Miles New | Transmission line miles on new rights of way (ROW)
Plan Status | Indicates status of project in planning or implementation. Conceptual, Proposed, Planned, Last Milestone Achieved, Under Construction and In Service
Estimated Cost | Total estimated facility cost
Cost Shared | Y if facility is cost shared per Attachment FF
Postage Stamp | Y if facility has postage stamp cost allocation per Attachment FF
MISO Facility | Y for facilities under MISO functional control. NT for non-transferred facilities under Agency Agreements

## Facilities
Target Appendix | Planning Region | Geographic Location by TO Member System | PrjID | Facility ID | Facility Type | Expected ISD | From Sub | To Sub | Ckt | Max kV | Min kV | Facility Rating | Description | State | Miles Upgrade | Miles New | Plan Status | Estimated Cost | Estimate Type | Est. Year Dollars | Comments | Emerg. Rating | Fac. Delay Reason | Cost Est. Variance | Submitting Comp. | Cost Shared | Postage Stamp
A in MTEP21 | South | AECC | 20161 | 25881 | SUB | 2024-01-01 | Selma South |  |  | 115 |  |  | 115/69 kV, 60/80/100 MVA transmission substation to be constructed on Entergy's transmission line from Monticello East to Reed. Expected to located south of Selma, AR. | AR |  |  | Proposed | 7500000 | Engineering Preliminary |  | Load will be transferred from Glendale to Selma South for normal operation. Selma South will be able to completely back feed 100% of the Glendale load for loss of the Glendale delivery point. |  |  |  | Arkansas Electric Coopertive Corporation | N | N
A in MTEP21 | South | AECC | 20265 | 25992 | CAP | 2024-01-01 | Star City |  |  | 69 |  |  | 9.6 MVAR Capacitor Bank | AR |  |  | Proposed | 1000000 | Planning Preliminary | [5 empty] | Arkansas Electric Coopertive Corporation | N | N
A in MTEP21 | West | ATC | 10590 | 21620 | LNrb | 2024-12-31 | Academy | Columbus | 1 | 69 |  | 79 | Rebuild Academy - Columbus 69kV. | WI | 1 |  | Proposed | 6300000 | Planning | 2024 |  | 108 |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 10590 | 25649 | SUB | 2024-12-31 | Columbus SS |  |  | 69 |  |  | Substation Asset Renewal | WI |  |  | Proposed | 2500000 | Planning | 2024 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 14964 | 23465 | SUB | 2025-06-30 | NA |  |  | 345 | 69 |  | Small Capital Project and Asset Renewal 2022 | WI,MI |  |  | Proposed | 52320773 | [6 empty] | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 14965 | 23468 | COM | 2025-06-30 | NA |  |  | 345 | 69 |  | Communication Reliability Upgrades 2022 | WI,MI |  |  | Proposed | 19252066 | [6 empty] | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 14966 | 23471 | LNup | 2025-06-30 | NA |  |  | 345 | 69 |  | Line Clearance Mitigation Projects 2022 | WI,MI |  |  | Proposed | 2832841 | [6 empty] | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 14967 | 23474 | SUB | 2025-06-30 | NA |  |  | 345 | 69 |  | Physical Security 2022 | WI,MI |  |  | Proposed | 11797871 | Planning | 2025 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 14968 | 23479 | SUB | 2025-06-30 | NA |  |  | 138 | 69 |  | Distribution Interconnection 2022 | WI,MI |  |  | Proposed | 27586994 | Planning | 2025 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 16489 | 24314 | SUB | 2024-12-31 | Empire SS |  |  | 138 | 138 |  | Asset renewal of circuit breakers, PT's, relays, switches and install new control building | MI |  |  | Proposed | 9900000 | Planning | 2024 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 16490 | 24316 | SUB | 2024-12-01 | Granville |  |  | 345 | 138 |  | Granville SS Asset Renewal | WI |  |  | Proposed | 28950000 | Planning | 2024 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 18048 | 24828 | LNrb | 2024-12-31 | Lincoln | Bluemound | 5053 | 138 |  |  | Line Rebuild - Underground | WI |  |  | Proposed | 35800000 | Scoping | 2024 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 19105 | 25387 | SUB | 2022-06-01 | Nelson Dewey |  |  | 138 | 69 |  | Substation Asset Renewal | WI |  |  | Proposed | 6170000 | Planning | 2022 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 19587 | 25516 | COM | 2024-12-31 | Petenwell | Council Creek | X-40 | 138 |  |  | Structure Replacement and OPGW Addition | WI |  |  | Proposed | 9000000 | Planning | 2024 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 19705 | 25540 | SUB | 2024-12-31 | Crivitz |  |  | 138 |  |  | Asset Renewal | WI |  |  | Proposed | 4599154 | Planning | 2024 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 19706 | 25541 | SUB | 2024-12-01 | North Appleton SS |  |  | 345 |  |  | Asset Renewal | WI |  |  | Proposed | 7938249 | Planning | 2024 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 19729 | 25549 | SUB | 2023-11-30 | Superior SS |  |  | 345 |  |  | Network Upgrades | WI |  |  | Proposed | 15621555 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | Y | Y
A in MTEP21 |  | ATC | 19729 | 25555 | SUB | 2023-11-30 | Superior SS |  |  | 345 |  |  | Interconnection Facilities | WI |  |  | Proposed | 1157933 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 19729 | 25554 | SUBmisc | 2023-11-30 | Arrowhead SS |  |  | 345 | 230 |  | Grounding Improvements | WI |  |  | Proposed | 1291386 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | Y | N
A in MTEP21 |  | ATC | 19729 | 25553 | SUBmisc | 2023-11-30 | Stone Lake SS |  |  | 345 |  |  | Grounding Improvements | WI |  |  | Proposed | 419936 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | Y | Y
A in MTEP21 |  | ATC | 19729 | 25552 | SUBmisc | 2023-11-30 | Arrowhead SS |  |  | 345 | 230 |  | Arrowhead SS Relay Upgrades | WI |  |  | Proposed | 535063 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | Y | N
A in MTEP21 |  | ATC | 19729 | 25551 | SUBmisc | 2023-11-30 | Stone Lake SS |  |  | 345 |  |  | Stone Lake SS Relay Upgrades | WI |  |  | Proposed | 423319 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | Y | Y
A in MTEP21 | West | ATC | 19729 | 25550 | LNup | 2023-11-30 | Arrowhead SS | Stone Lake SS | 651 | 345 |  |  | Line 651/W25 Loop into Superior SS | WI |  |  | Proposed | 1796413 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | Y | Y
A in MTEP21 | West | ATC | 19806 | 25567 | SUB | 2023-06-01 | Bonnie Road SS |  |  | 69 |  |  | New substation DIC | WI |  |  | Proposed | 3504413 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 19959 | 25641 | COM | 2023-12-31 | Sussex | Bark River |  | 138 |  |  | OPGW Installation | WI |  |  | Proposed | 3766000 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 19961 | 25645 | LN | 2024-05-31 | West Marinette | Wells St |  | 69 |  |  | T-D Interconnection | WI |  |  | Proposed | 16100000 | Planning | 2024 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 19965 | 25972 | SUB | 2023-12-01 | National SS |  |  | 138 |  |  | • Relocate one 138 kV line position (line 16343) to a different bus position at National substation. • Install one +/- 50 MVA, 138 kV STATCOM (Static Synchronous Compensator) at National substation. o Include one spare 138 kV transformer o Add a new 138 kV circuit breaker and protection package at National | MI |  |  | Proposed | 24200000 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 20625 | 26056 | INT | 2022-06-01 | 7 Mile Creek SS |  |  | 138 |  |  | E&P Contract Cost | WI |  |  | Proposed | 5592161 | Planning | 2022 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 20625 | 26387 | INT | 2022-06-01 | 7 Mile Creek SS |  |  | 138 |  |  | Interconnection Facilities | WI |  |  | Proposed | 5592161 | Planning | 2022 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 20625 | 26386 | SUB | 2022-06-01 | Sand Lake SS |  |  | 138 |  |  | Transformer Replacement | WI |  |  | Proposed | 4752825 | Planning | 2022 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 20625 | 26385 | SUBmisc | 2022-06-01 | Port Edwards |  |  | 138 | 69 |  | Grounding Improvements | WI |  |  | Proposed | 220000 | Planning | 2022 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 20625 | 26384 | SUBmisc | 2022-06-01 | Wautoma SS |  |  | 138 | 69 |  | Remote End Work | WI |  |  | Proposed | 146602 | Planning | 2022 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 20625 | 26383 | SUBmisc | 2022-06-01 | Sand Lake SS |  |  | 138 |  |  | Remote End Work | WI |  |  | Proposed | 146602 | Planning | 2022 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 20625 | 26382 | SUBmisc | 2022-06-01 | Port Edwards SS |  |  | 138 | 69 |  | Remote End Work | WI |  |  | Proposed | 146602 | Planning | 2022 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 20625 | 26381 | LINE | 2022-06-01 | Wautoma SS | Port Edwards SS | X-11 | 138 |  |  | Sectionalization | WI |  |  | Proposed | 708668 |  | 2022 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 |  | ATC | 20625 | 26380 | SUB | 2022-06-01 | 7 Mile Creek SS |  |  | 138 |  |  | Network Upgrades | WI |  |  | Proposed | 258407 |  | 2022 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 20785 | 26092 | LNrc | 2023-05-15 | Highway V SS | Preble SS | X-154 | 138 |  |  | Reconductor to minimum 1300A two hour emergency, all seasons | WI |  |  | Proposed | 1777603 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | West | ATC | 20925 | 26116 | SUB | 2023-12-31 | Lancaster SS |  |  | 138 | 69 |  | Lancaster Transformer Replacement & Substation Rebuild | WI |  |  | Proposed | 3700000 | Planning | 2023 |  |  |  |  | American Transmission Co. LLC | N | N
A in MTEP21 | Central | AmerenIL | 9843 | 21220 | TX | 2017-05-26 | Normal East |  |  | 138 | 34.5 | 112 | Install 138-34.5 kV transformer. | IL |  |  | In Service | 1500000 | Engineering | 2016 |  | 112 |  | Initial cost estimate | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 13546 | 22640 | SUB | 2020-12-01 | County Highway 20 | 138 kV ring bus |  | 138 |  |  | Install new 3-position (ultimate 4-position) ring bus at the existing County Highway 20 substation location. | IL |  |  | M5_In Service | 6800000 | Actual | 2019 |  |  | Re-evaluated timing of the project. |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 16989 | 24455 | SUB | 2023-12-01 | Mattoon West | Substation |  | 138 |  |  | Install new 6 position ultimate ring bus at Mattoon West Substation. | IL |  |  | Planned | 8500000 | Engineering | 2019 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 16990 | 24456 | SUB | 2022-06-01 | Wanda | Substation |  | 138 |  |  | Install new 6 position ultimate ring bus at Wanda Substation. | IL |  |  | Planned | 7200000 | Engineering | 2019 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 17864 | 24694 | CB | 2022-12-01 | Cahokia |  |  | 138 |  |  | Replace OCB H27 on the C-GRAT-3 position and OCB H35 on the C-RUSL-2 positon with symetrically rated SF6 55 kA circuit breakers. | IL |  |  | Planned | 4200000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 17979 | 24750 | SUB | 2022-12-01 | North Staunton | Substation |  | 138 |  |  | Rebuild the North Stauton 138 kV substation to a ring bus configuration. | IL |  |  | Planned | 16200000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 18074 | 24856 | CB | 2022-06-01 | Jacksonville IP | Substation |  | 138 |  |  | Replace 138 kV breaker JCKI-138KV BT 1-2 BKR 1302 at Jacksonville Industrial Park Substation. | IL |  |  | Planned | 1300000 | Budgetary | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 18889 | 25339 | LNrb | 2023-12-01 | Hickok | North LaSalle | 1659 | 138 |  |  | Rebuild to 2000A | IL |  |  | Planned | [7 empty] | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 19025 | 25370 | SwSta | 2022-11-01 | Yvonne |  |  | 138 |  |  | New station for Hickory Point Wind Generator J815 | IL |  |  | Planned | 5700000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 19026 | 25371 | TEQ | 2023-10-01 | Pana |  |  | 138 |  |  | New position for J912 | IL |  |  | Planned | 900000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 19085 | 25382 | BUS | 2022-06-01 | Shelbyville S. |  |  | 138 |  |  | Rebuild to 6 position ultimate ring | IL |  |  | Planned | 10000000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 19345 | 25464 | SUB | 2024-06-01 | Valmeyer |  |  | 138 | 34.5 |  | Valmeyer 138 kV Substation Ring Bus and add 138/34.5 kV Transformer | IL |  |  | Planned | 5900000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 19826 | 25568 | CB | 2025-12-01 | Dupo Ferry |  |  | 138 |  |  | Replace overstressed breakers | IL |  |  | Planned | [7 empty] | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 19956 | 25638 | LNrc | 2022-12-01 | Louisville | Jasper |  | 138 |  |  | Rebuild 23 miles to 2000 A. | IL |  |  | Planned | 7900000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 19988 | 25658 | TX | 2023-12-01 | Roxford |  |  | 345 | 138 |  | Add 2nd 345/138 kV transformer | IL |  |  | Planned | 10200000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 20079 | 25781 | SUB | 2021-12-31 | Butler 69 |  |  | 69 | 12 |  | Rebuild Butler sub with new 5/6.25MVA 3ph transformer, relocate existing regulators, replace all switches. | IL |  |  | Planned | 1800000 | [6 empty] | Wabash Valley Power Association, Inc. | N | N
A in MTEP21 | Central | AmerenIL | 20184 | 25946 | SwSta | 2024-12-01 | Ring bus North of RS Wallace |  |  | 138 |  |  | Ring bus North of RS Wallace that ties together RS Wallace - Spring Bay and CAT2 - Hines 138 kV lines. | IL |  |  | Planned | 8700000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 20187 | 25949 | TEQ | 2025-12-01 | Chesterville |  |  | 138 | 69 |  | Add 2 line breakers | IL |  |  | Planned | 1700000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 20188 | 25951 | SUB | 2025-12-01 | Gibson City S |  |  | 138 | 69 |  | Add 5 position ring bus | IL |  |  | Planned | 7000000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 20191 | 25953 | SUB | 2024-12-01 | Marion N |  |  | 138 | 69 |  | Add ring bus | IL |  |  | Planned | 8000000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 20285 | 25995 | SUB | 2022-12-01 | Herrin East |  |  | 138 |  |  | Install initial 4-position ring bus at the Herrin East substation Location | IL |  |  | Planned | 7500000 | Engineering | 2019 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 20365 | 26008 | TX | 2022-06-01 | Normal East |  |  | 138 | 69 |  | Install new 112 MVA, 138-69 kV Transformer | IL |  |  | Planned | 2000000 | Engineering | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 20425 | 26034 | TEQ | 2022-12-01 | Holland |  |  | 138 |  |  | Remove CT limit | IL |  |  | Planned | 500000 | Engineering | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 20465 | 26036 | TX | 2021-10-05 | Commodore |  |  | 345 | 230 |  | 345/230 kV transformer | IL |  |  | Planned | [7 empty] | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL | 21045 | 26133 | LNrl | 2021-12-01 | ADM North | Mt. Zion |  | 138 |  |  | Relocate 0.6 miles of existing 138 kV ADM North-Mt. Zion Route 121-1616 to single circuit, single shaft steel poles. The entire section has distribution underbuild. Roughly structures 10A-14. | IL |  |  | Planned | 3500000 | Budgetary | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 |  | AmerenIL | 21325 | 26235 | LNrb | 2022-06-01 | Rossville | Vermilion |  | 138 |  |  | Rebuild the Rossville-Vermilion-1305 138 kV circuit with 2000 A summer emergency capability conductor. Also, install OPGW. | IL |  |  | Planned | 12800000 | Budgetary | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 |  | AmerenIL | 21585 | 26291 | LNrb | 2022-12-01 | Decatur East Main St | Route 51 Decatur |  | 138 |  |  | Rebuild AMIL East Main St-Route 51 Decatur – 1416 138 kV line | IL |  |  | Planned | 4200000 | Budgetary | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL, AmerenMO | 20193 | 25959 | CB | 2022-12-01 | Various |  |  | 345 | 138 |  | Dollars assume 15 breakers replaced each year at a cost of $300k each. | IL,MO |  |  | Proposed | 4500000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 |  | AmerenIL, AmerenMO | 20193 | 25961 | CB | 2024-12-01 | Various |  |  | 345 | 138 |  | Dollars assume 15 breakers replaced each year at a cost of $300k each. | IL,MO |  |  | Proposed | 4500000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 |  | AmerenIL, AmerenMO | 20193 | 25960 | CB | 2023-12-01 | Various |  |  | 345 | 138 |  | Dollars assume 15 breakers replaced each year at a cost of $300k each. | IL,MO |  |  | Proposed | 4500000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL, AmerenMO | 20194 | 25956 | RLY | 2022-12-01 | Various |  |  | 345 | 138 |  | 70 sites were identified with obsolete electromechanical relays and/or carrier equipment. Dollars assume 23 sites are addressed each year at a cost of $150k per site. | IL,MO |  |  | Proposed | 3450000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 |  | AmerenIL, AmerenMO | 20194 | 25958 | RLY | 2024-12-01 | Various |  |  | 345 | 138 |  | 70 sites were identified with obsolete electromechanical relays and/or carrier equipment. Dollars assume 23 sites are addressed each year at a cost of $150k per site. | IL,MO |  |  | Proposed | 3450000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 |  | AmerenIL, AmerenMO | 20194 | 25957 | RLY | 2023-12-01 | Various |  |  | 345 | 138 |  | 70 sites were identified with obsolete electromechanical relays and/or carrier equipment. Dollars assume 23 sites are addressed each year at a cost of $150k per site. | IL,MO |  |  | Proposed | 3450000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenIL, AmerenMO | 20195 | 25962 | LNup | 2022-12-01 | Various |  |  | 345 | 138 |  | Pole and Insulator replacements requested by Maintenance. | IL,MO |  |  | Proposed | 41000000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 |  | AmerenIL, AmerenMO | 20195 | 25964 | LNup | 2024-12-01 | Various |  |  | 345 | 138 |  | Pole and Insulator replacements requested by Maintenance | IL,MO |  |  | Proposed | 24500000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 |  | AmerenIL, AmerenMO | 20195 | 25963 | LNup | 2023-12-01 | Various |  |  | 345 | 138 |  | Pole and Insulator replacements requested by Maintenance | IL,MO |  |  | Proposed | 32000000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenMO | 9830 | 21206 | LNrc | 2021-12-31 | Meramec | Joachim | 2 | 138 | 138 | 322 | Reconductor to 1600 A summer emergency capability. | MO | 15.91 |  | Planned | 300000 | Budgetary | 2019 |  | 382 |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenMO | 17344 | 24528 | SUB | 2021-12-01 | Berkeley | Substation |  | 138 |  |  | Replace 138 kV bus tie 1-2 and 2-3 breakers. Upgrade position to 2000A | MO |  |  | Planned | 1300000 | Budgetary | 2019 | Scope Reduction of moving line breakers and CS to a new reliability project. |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenMO | 19827 | 25569 | CB | 2025-12-01 | Sioux |  |  | 345 | 138 |  | Replace overstressed breaker | MO |  |  | Planned | 700000 | Budgetary | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenMO | 19852 | 25580 | SwSta | 2022-12-01 | Comstock |  |  | 161 | 161 |  | 161kV breaker-and-a-half substation to interconnect Ameren's Miner-Sikeston line and Sikeston Board of Municipal Utilities' New-Madrid-Sikeston 161kV line | MO |  |  | Planned | 5000000 | Budgetary | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 |  | AmerenMO | 19852 | 26201 | LN | 2022-12-01 | Reelfoot | New Madrid |  | 161 |  |  | Reelfoot-New Madrid 161 kV line | MO |  |  | Planned | 3200000 | Budgetary | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 |  | AmerenMO | 19852 | 25581 | SwSta | 2022-12-01 | Reelfoot |  |  | 161 | 161 |  | Construct new 161kV ring bus near New Madrid and extend SBMU's 161kV in/out of the ring bus. The City of New Madrid will install a 161/69kV xfmr to serve new industrial customer. | MO |  |  | Planned | 7000000 | Budgetary | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenMO | 19968 | 25651 | INT | 2022-06-01 | Zachary | Maywood |  | 345 |  |  | Zachary-Maywood 345 kV New Ring Bus for J1025 Generator Interconnection | MO |  |  | Planned | 9800000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenMO | 19969 | 25652 | CAP | 2025-06-02 | Belleau |  |  | 345 | 138 |  | Belleau 345/138 kV Substation - Install 138 kV capacitor bank | MO |  |  | Planned | 3500000 | Budgetary | 2021 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenMO | 20065 | 25780 | SUB | 2020-09-03 | New Bourbon 69 |  |  | 69 |  |  | Replace 69 kV brkrs B24, B25, B26, B39, & B40 at New Bourbon Sub due to age and condition. Also purchase a spare brkr. Install GPS clocks and wire to the microprocessor relays, Remove the relay 67 directional overcurrent tripping elements for the xfmr. | MO |  |  | Planned | 1200000 | Engineering | [5 empty] | Wabash Valley Power Association, Inc. | N | N
A in MTEP21 | Central | AmerenMO | 20069 | 25778 | SUBmisc | 2020-12-31 | Salem Bulk |  |  | 69 | 12 |  | Install a new SEL data concentrator, Install GPS clocks and wire the GPS clocks to the microprocessor relays, Remove the relay 67 directional overcurrent tripping elements. | MO |  |  | Planned | 100000 | Engineering | [5 empty] | Wabash Valley Power Association, Inc. | N | N
A in MTEP21 | Central | AmerenMO | 20070 | 25775 | SUB | 2021-12-31 | Trail of Tears | Trail of Tears |  | 69 | 69 | 81 | Replace the four oil filled 69 kV breakers at Trail of Tears to fix identified constraints for CT availability of the new bus differentials | MO |  |  | Planned | 2800000 | Engineering |  |  | 81 |  |  | Wabash Valley Power Association, Inc. | N | N
A in MTEP21 | Central | AmerenMO | 20072 | 25774 | LNrb | 2021-06-01 | Seminary (Perryville) | Park | 1 | 69 | 69 | 81 | Upgrade 3.06 mi. 3/0ACSR to 477ACSR of 69kV Line T17 from Seminary to Line B43 Park tap switch 117. Add 48 fiber OPGW entire 3.06 miles. | MO | 3.06 | 0 | Planned | 2000000 | Engineering |  |  | 81 |  |  | Wabash Valley Power Association, Inc. | N | N
A in MTEP21 | Central | AmerenMO | 20156 | 25870 | CAP | 2022-12-01 | Galena |  |  | 161 |  |  | Install 28.8 MVAR capacitor bank | MO |  |  | Planned | 900000 | Budgetary | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenMO | 21125 | 26148 | INT | 2022-10-01 | Burns |  |  | 345 |  |  | New 3 position ring bus for 250 MW solar J1145 | MO |  |  | Planned | 1100000 | Engineering | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | AmerenMO | 21125 | 26149 | SwSta | 2022-10-01 | Montgomery | McCredie |  | 345 |  |  | New 3 position ring bus to connect J1145 250 MW solar | MO |  |  | Planned | 9000000 | Engineering | 2020 |  |  |  |  | Ameren Services Company | N | N
A in MTEP21 | Central | BREC | 3439 | 6342 | SUB | 2024-12-31 | Ensor 161 kV | Ensor 69 kV |  | 161 | 69 | 56 MVA | new substation | KY |  |  | Proposed | 5400000 | Planning | 2010 |  | 56 MVA |  |  | Big Rivers Electric Corporation | N | N
A in MTEP21 |  | BREC | 3439 | 25559 | CAP | 2024-12-31 | Ensor |  |  | 69 |  | 30 MVAR | add capacitor at proposed substation | KY |  |  | Proposed | 400000 | [6 empty] | Big Rivers Electric Corporation | N | N
A in MTEP21 | Central | BREC | 18605 | 25232 | GEN | 2021-04-01 | Hardinsburg |  |  | 161 |  |  | 100 MW solar per J753 | KY |  |  | Proposed | 0 | Budgetary | [5 empty] | Big Rivers Electric Corporation | N | N
A in MTEP21 | Central | BREC | 18605 | 25233 | TEQ | 2021-04-01 | Hardinsburg |  |  | 161 |  |  | Terminal equipment necessary to connect 100 MW solar facility J753 | KY |  |  | Proposed | 200000 | Budgetary | [5 empty] | Big Rivers Electric Corporation | N | N
A in MTEP21 | Central | BREC | 18606 | 25234 | GEN | 2021-04-01 | Meade County |  |  | 161 |  |  | 200 MW Solar facility addition at Meade County (J762) | KY |  |  | Proposed | 0 | Budgetary | [5 empty] | Big Rivers Electric Corporation | N | N
A in MTEP21 | Central | BREC | 18606 | 25235 | TEQ | 2021-04-01 | Meade County |  |  | 161 |  |  | Terminal equipment needed to connect 200 MW solar facility (J762) at Meade County | KY |  |  | Proposed | 500000 | Budgetary | [5 empty] | Big Rivers Electric Corporation | N | N
A in MTEP21 | Central | BREC | 19006 | 25367 | LN | 2020-11-03 | Tap near Beda | Hartford (KU) | 1 | 69 |  | 72 | 69 kV normally open - emergency use on an as-available basis | KY |  | 0.1 | Proposed | 0 |  |  | only a small portion of the connection will be owned by BREC. KU is constructing and funding the addition. | 88 |  |  | Big Rivers Electric Corporation | N | N
A in MTEP21 | Central | BREC | 21165 | 26233 | Dist |  | Maxon |  |  | 69 |  |  | Expansion to serve new load from existing 69 kV substation | KY |  |  | Proposed | 1200000 | [6 empty] | Big Rivers Electric Corporation | N | N
A in MTEP21 | Central | BREC | 21165 | 26234 | LNrb |  | McCracken County |  |  | 161 |  |  | Overbuild 161 kV on existing 69 kV ROW. Reconductor existing 69 kV during overbuild. | KY |  |  | Proposed | 10200000 | [6 empty] | Big Rivers Electric Corporation | N | N
A in MTEP21 | Central | BREC | 21387 | 26251 | CAP |  | Hancock County |  |  | 69 |  |  | 35 MVar capacitor bank addition to the existing Hancock County substation. | KY |  |  | Proposed | 500000 | Budgetary | [5 empty] | Big Rivers Electric Corporation | N | N
A in MTEP21 | South | CLECO | 13874 | 23298 | SUB | 2022-07-01 | Ball |  |  | 230 |  |  | Tap a new 230 kV substation into and out of the current Donahue to Sherwood 230 kV line. Move 16 MW of load from Beaver Creek to be served out of this new substation | LA |  |  | Proposed | 8130000 | Planning | [5 empty] | Cleco Power LLC | N | N
A in MTEP21 | South | CLECO | 21169 | 26167 | CAP | 2023-06-01 | Bayou Sale | Pelican |  | 138 |  |  | Move the existing cap bank from Bayou Sale to Pelican. | LA |  |  | Proposed | 700000 | Planning | [5 empty] | Cleco Power LLC | N | N
A in MTEP21 | South | CLECO | 21207 | 26185 | LNrl | 2023-12-01 | North Slidell | Tailsheek | 1 | 230 |  |  | Move transmission line for Airport Expansion | LA |  |  | Proposed | 5300000 | Planning Preliminary | [5 empty] | Cleco Power LLC | N | N
A in MTEP21 | South | CLECO | 21207 | 26186 | LNrl | 2023-12-01 | North Slidell | Cane Bayou | 1 | 230 |  |  | Line move for Airport Expansion | LA |  |  | Proposed | 4500000 | Planning Preliminary | [5 empty] | Cleco Power LLC | N | N
A in MTEP21 | West | CMMPA | 20166 | 25899 | TX | 2021-04-05 | Delano8 |  |  | 69 |  |  | Delano is planning to replace the Sub A transformer with a new 12/16/20 MVA 69/12.47kV transformer. This new transformer will meet the load growth forecasted for the city and provide reliability for its customers. Reconfiguration within the substation may also allow for more customers to be served in the event one of the two 69kV transformers is out of service. | MN |  |  | Proposed | 1750000 | Planning | [5 empty] | Central Minnesota Municipal Power Agency | N | N
A in MTEP21 | West | CMMPA | 20168 | 25902 | TX | 2022-04-04 | Delano 8 |  |  | 69 |  |  | Delano is planning to replace substation B transformer with new 12/16/20 MVA 69/12.47kV transformer. This new transformer will meet the load growth forecasted for the city and provide reliability for its customers. Reconfiguration within the substation may also allow for more customers to be served in the event one of the two 69kV transformers is out of service. This solution also includes a new fire wall between the new transformers and additional distribution feeders for load transfer. | MN |  |  | Proposed | 2500000 | Planning | [5 empty] | Central Minnesota Municipal Power Agency | N | N
A in MTEP21 | West | CMMPA | 20169 | 25903 | SUB | 2022-04-04 | DELANO 8 |  |  | 69 |  |  | Delano is planning to build a new 69kV substation to serve expected residential and future industrial park load growth on the NW side of the city. | MN |  |  | Proposed | 4100000 | Planning | [5 empty] | Central Minnesota Municipal Power Agency | N | N
A in MTEP21 | Central | CWLD | 19805 | 25566 | LN | 2025-09-01 | Grindstone 69 kV | UMC 69 kV | 1 | 69000 | 13800 |  | Build a new substation with a 69/13.8 kV transformer at UMC. Build a new 69 kV ringbus at UMC. Disconnect Grindstone-Hinkson Creek (HC) 69 kV line at HC and connect it to new UMC ringbus. | MO |  |  | Planned | 26000000 | Engineering Preliminary | [5 empty] | City of Columbia, MO | N | N
A in MTEP21 | Central | DEI | 20174 | 25933 | CAP | 2023-06-01 | Sullivan 69kV |  |  | 69 |  |  | Install 19.8MVAR - 69kV cap | IN |  |  | Proposed | 500000 | Planning Preliminary | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20181 | 25942 | CB | 2022-12-31 | Five Points |  |  | 138 |  |  | Replace (5) 138kV oil circuit breakers with SF6 gas circuit breakers - 13803, 13804, 13809, 13813, and 138kV Bus tie breaker; 13803,04,13 were identified in 2020 as overdutied in the DEI short ckt analysis by P&C Eng'g | IN |  |  | Proposed | 4987000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20190 | 25955 | LNrb | 2022-12-31 | Monroe City Jct | Petersburg Jct |  | 138 | 69 |  | 6960 Pt 3 Rbld Monroe City Jct_Petersburg Jct w/ 477acsr - 6.25 miles. Reconductor 2.4 miles of circuit 13825 (structures #844-1162 to #844-1190/#844-3100) and 1.2 miles of circuit 13838 where they are double-circuited with 6960. Replace Monroe City Jct #1 and #2 switches and rename to 69-1 and 69-2. Rebuild the line at the Petersburg Jct (poles #821-1322 through 821-1327). | IN | 9.85 |  | Proposed | 10010000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20196 | 25965 | Dist | 2022-06-01 | Rosston 69/12kV sub |  |  | 69 | 12 |  | new sub to be fed from the 69182 ckt and will replace existing Whitestown 69/12kV sub in the 6983 ckt. | IN |  |  | Proposed | 1337000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20197 | 25967 | SUB | 2022-12-31 | Wabash 138 |  |  | 138 | 69 |  | Upgrade misc 69kV station equipment and convert 138kV straight bus to ring bus | IN |  |  | Proposed | 12570000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20198 | 25968 | SUB | 2022-12-31 | Hortonville |  |  | 345 | 69 |  | Replace line relays: 34504, 34527, 6917, 69142, 69155. Install equipment to convert 345kV bus to ring bus config. | IN |  |  | Proposed | 1871000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20199 | 25969 | SUB | 2022-12-31 | Tipton West |  |  | 230 |  |  | reconfigure 230kV bus to ring configuration | IN |  |  | Proposed | 1864000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20200 | 25970 | SUB | 2022-12-31 | Noblesville Generating Station |  |  | 138 | 69 |  | replace 138/69/2.4kV Bk9; misc upgrades to 138kV relays and wave traps, etc. | IN |  |  | Proposed | 4328000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20205 | 25973 | LN | 2021-12-08 | Greenwood Clark Twnshp | HE Willard Green |  | 69 |  | 150 | expand ring bus and add 69165 line terminal at Clark Twnshp; build short line to HE Willard Green | IN |  | 0.2 | Proposed | 4056000 | Engineering w/AFUDC | 2020 |  | 150 |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20206 | 25974 | LNrb | 2022-12-31 | Huntington 138 | Meridian Rd Jct |  | 69 |  |  | 6923 Part 2 rebuild with 954acsr; replace switches at Erie Stone jct | IN | 1.4 |  | Proposed | 4006000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20207 | 25975 | LNrb | 2022-12-31 | Loogootee Jct. | Loogootee |  | 69 |  | 100 | Rebuild transmission line 69194 from Loogootee Jct (pole #816-2001 through #816-2152). Approx 10.2 miles. Approx 152 poles. Replace Loogootee Jct #1, #2, and #3 switches. Replace H.E. Bramble #1 and #2 switches. | IN | 10.2 |  | Proposed | 13761000 | Engineering w/AFUDC | 2020 |  | 100 |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20208 | 25976 | LNrb | 2022-12-31 | Morgantown | Bean Blossom |  | 69 |  | 100 | Rebuild transmission line 6949 from Morgantown substation (pole #825-3122) to Bean Blossom substation (pole #825-3270) using light duty steel poles, 477 ACSR | IN | 8.4 |  | Proposed | 13353000 | Engineering w/AFUDC | 2020 |  | 100 |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20225 | 25977 | LNrb | 2022-12-31 | McKay Rd. Jct. | HE Lewis Crk. Jct. |  | 69 |  | 100 | Rebuild transmission line 6975 from McKay Rd Junction (pole #807-3096) to H.E. Lewis Creek Junction (pole #807-3168) using light duty steel poles, 477 ACSR conductor and OPGW. - 5.9 miles ; Replace two switches at McKay Rd Junction 2000A | IN | 5.9 |  | Proposed | 7244000 | Engineering w/AFUDC | 2020 |  | 100 |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20226 | 25978 | SUB | 2022-12-31 | Deedsville 345 |  |  | 345 | 69 |  | Reconfigure 345kV to ring bus. Replace various 345kV and 69kV transmission equipment including relays and OCBs | IN |  |  | Proposed | 7710000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20227 | 25979 | SUB | 2022-12-31 | Middlefork |  |  | 69 |  |  | Replace misc. 69kV OCBs and relays; replace 6910-01 line switch with 2000A; establish 69kV ring bus | IN |  |  | Proposed | 8713000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20228 | 25980 | SUB | 2022-12-31 | Prescott |  |  | 345 | 69 |  | Replace misc. 69kV OCBs and relays; establish 345kV ring bus | IN |  |  | Proposed | 7543000 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20230 | 25981 | LNrb | 2023-12-31 | Laf. Cincinnati St. | Purdue NW tap |  | 138 |  | 301 | Rebuild the 13820 line from the Purdue Northwest Tap to West Lafayette Purdue University to Cincinnati St. substation using 954 ACSR at 120 C | IN | 4.79 |  | Proposed | 9580000 | Planning Preliminary | 2021 |  | 301 |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20245 | 25983 | GEN | 2022-02-15 | Gwynneville Solar | Gwynneville 345 |  | 345 | 0.6 | 199 | J805 Gwynneville Solar (Speedway Solar LLC) - The Generating Facility is composed of sixty-seven (67) HEM inverter units rated at 3.3 MVA each. Interconnection Service provided under this agreement is 199 MW of conditional ERIS that will become 199 MW of ERIS and/or 199 MW of NRIS where the NRIS will become 199 MW upon completion of all Network Upgrades; collector substation shall contain one (1) generator step-up transformer 34.5/345 kV, 132/176/220 MVA; Point of Interconnection shall be at the terminal position between breakers 345NEW-23 and 34515-NEW at the existing Gwynneville Sub; Approximately 0.5 mile long 345kV lead line; | IN |  | 0.5 | Planned | 3026518 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 |  | DEI | 20245 | 25985 | SUB | 2022-02-15 | Gwynneville 345 |  |  | 345 |  |  | J805 Gwynneville 345 expand ring bus for gen POI - between breakers 345NEW-23 and 34515-NEW | IN |  |  | Planned | 1346706 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 |  | DEI | 20245 | 25984 | LNrb | 2021-12-31 | Morristown | HE Van Buren |  | 69 |  | 100 | Circuit 69166 Network Upgrade - rebuild with 477ACSR - 4.82 miles of 4/0 ASCR6x1 | IN | 4.82 |  | Planned | 3284433 | Engineering w/AFUDC | 2020 |  | 100 |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20246 | 25986 | GEN | 2022-08-19 | Fairbanks Solar | Fairbanks Sw Sta |  | 345 | 0.63 | 250 | J829 - Fairbanks Solar Energy Center ( Fairbanks Solar Energy Center LLC): sixty (60) TMEIC PV Ninja inverter units rated at 4.2 MVA each. Interconnection Service provided under this agreement is 250 MW of conditional ERIS that will become 250 MW of ERIS and/or NRIS upon completion of all Network Upgrades ; collector substation shall contain two (2) generator step-up transformers 34.5/345 kV, 66/88/110MVA ; Point of Interconnection shall be at the terminal position between breakers 345SF-NEW and 34520-SF ; 0.5 miles of 345 kV generator leadline ; | IN |  | 0.5 | Planned | 1724639 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 |  | DEI | 20246 | 25987 | SwSta | 2022-08-19 | Fairbanks Sw Sta |  |  | 345 |  |  | J829 - Fairbanks Sw'g. Sta. (3 CB ring) to be inserted in the Dresser - Merom 34520 line approx 13 mi S. of Dresser; (Merom - Fairbanks = 34550; Fairbanks - solar farm = 34551; Fairbanks - Dresser = 34520); will require replacing the wave trap and line tuning equipment at Dresser station; | IN |  |  | Planned | 13723359 | Engineering w/AFUDC | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20247 | 25988 | LNrb | 2023-06-01 | Lafayette South | Lafayette Shadeland |  | 138 |  | 291 | Rebuild 138100 ckt Laf South to Shadeland with 954ACSR@120C - 3.2 miles; upgrade Shadeland 795AL bus to 954AL | IN | 3.2 |  | Proposed | 7500000 | Planning Preliminary | 2021 |  | 291 |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20248 | 25989 | SUB | 2023-06-01 | Dresser 345 |  |  | 345 |  |  | Dresser 345kV Redundant Ckt Brkr Addition between Bk1 and Bk2 with fully redundant protection scheme per future P5 definition | IN |  |  | Proposed | 8000000 | Planning Preliminary | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20250 | 25991 | LN | 2022-04-01 | DEI Bolivar | NIPS Templeton |  | 69 |  | 100 | WVPA to construct new N.O. reserve 69kV line to existing NIPS Templeton sub from DEI Bolivar | IN |  | 6.7 | Proposed | 7000000 | Planning Preliminary | 2020 |  |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | Central | DEI | 20645 | 26062 | SUB | 2021-10-01 | Greenfield Hastings Park | ring bus |  | 138 |  |  | Greenfield Hastings Park - establish a 3-breaker, 138kV, ring bus | IN |  |  | Proposed | 4237000 | Engineering w/AFUDC | 2020 | needs to be moved to Target A in MTEP21 |  |  |  | Duke Energy Corporation | N | N
A in MTEP21 | West | DPC | 19953 | 26086 | LNrb | 2023-04-14 | Frenchville | Ettrick | 1 | 69 |  |  | Rebuild 11.1 miles of the N-223 line from the N-122 tap to the XEL Ettrick substation with 4/0 conductor. | WI | 11.1 |  | Planned | 3848576.89 | Planning | 2020 |  |  |  |  | Dairyland Power Cooperative | N | N
A in MTEP21 | West | DPC | 20136 | 26085 | LNrb | 2024-02-09 | Pine Lake | Dunn Ethanol | 1 | 69 |  |  | This project is a mix of a rebuild of DPC’s existing 69 kV line in the area and construction on new right-of-way. The recommended plan in this area is to construct new transmission line with 477 ACSR conductor, a mix of replacement of existing line and new right-way from XEL’s Pine Lake transmission substation to the east towards the Dunn Ethanol distribution substation. The recommended plan will address the age and condition issues, constructing the line with new poles and 477 ACSR conductor. The plan will also address the longer tap lines to distribution substations with individual taps to all five distribution substations served from this line. Finally, building to the Dunn Ethanol distribution substation will provide backup service. | WI | 22.15 | 0.58 | Planned | 13051779.51 | Planning | 2020 |  |  |  |  | Dairyland Power Cooperative | N | N
A in MTEP21 | South | Entergy-AR | 19907 | 25593 | Dist | 2022-12-30 | Moreland |  |  | 161 |  |  | Rebuild the existing Moreland 161kV substation | AR |  |  | M3_Long Lead Materials | 13400000 | Pre-Construction | [5 empty] | Entergy Arkansas | N | N
A in MTEP21 | South | Entergy-AR | 19908 | 25594 | TX | 2023-06-01 | Cave City |  |  | 161 | 34.5 |  | Add a 40 MVA LTC 161/34.5kV transformer | AR |  |  | M1_Final SPM or OOC | 8054670 | Planning | [5 empty] | Entergy Arkansas | N | N
A in MTEP21 | South | Entergy-AR | 19909 | 25599 | TEQ | 2021-12-30 | N/A |  |  | 500 | 115 |  | The AM renewal program to address aging and failing transmission assets | AR |  |  | M4_Pre-Construction | 27200000 | Budgetary | [5 empty] | Entergy Arkansas | N | N
A in MTEP21 | South | Entergy-AR | 19910 | 25600 | TEQ | 2022-12-30 | N/A |  |  | 500 | 115 |  | The AM renewal asset program to address aging and failing transmission assets | AR |  |  | M1_Final SPM or OOC | 19300000 | Budgetary | [5 empty] | Entergy Arkansas | N | N
A in MTEP21 | South | Entergy-AR | 21447 | 26275 | INT | 2023-03-15 | Happy 115kV |  |  | 115 |  |  | New three breaker ring bus switching station to interconnect J1373 | AR |  |  | M1_Final SPM or OOC | 3717000 | GIA | 2020 |  |  |  |  | Entergy Arkansas | N | N
A in MTEP21 | South | Entergy-LA | 15605 | 24199 | LNrc | 2021-12-01 | Tezcuco | Frisco | 1 | 230 |  |  | Increase the rating of the Tezcuco to Frisco 230 circuit #1 and #2 to a minimum of 1925A (765 MVA). | LA |  |  | Proposed | 2200000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 15605 | 24200 | LNrc | 2021-12-01 | Tezcuco | Frisco | 2 | 230 |  |  | Increase the rating of the Tezcuco to Frisco 230 circuit #1 and #2 to a minimum of 1925A (765 MVA). | LA |  |  | Proposed | [7 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 18228 | 25054 | LNrb | 2022-02-28 | Golden Meadow | Clovelly |  | 115 |  |  | Rebuild the ~7 mile Golden Meadow to Clovelly 115 kV line to 230 kV specifications. | LA |  |  | Proposed | 86300000 | Planning |  | Energized construction due to radial line |  |  |  | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 19957 | 25639 | TEQ | 2022-06-01 | Lake Arthur |  |  | 69 |  |  | Replace switch 732 at Lake Arthur with a motorized load break switch that has whips and bottles. Move the Normally Open point from switch 8873 to switch 732 so that Lake Arthur 69 kV station is fed out of Lawtag 69 kV station. | LA |  |  | Proposed | 706000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 19987 | 25659 | BAT | 2023-12-01 | Nelson |  |  | 230 | 138 |  | Ensure dual battery installations or monitoring sufficient to FERC 754 guidelines at Nelson 230 kV and 138 kV. | LA |  |  | Proposed | [7 empty] | Entergy | N | N
A in MTEP21 |  | Entergy-LA | 19987 | 25660 | RLY | 2023-12-01 | Nelson |  |  | 230 | 138 |  | Ensure coordination with PowerGen on GSU high speed dual primary protection for all generation at Nelson | LA |  |  | Proposed | 17900000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 20039 | 25737 | TEQ | 2021-12-31 | All |  |  | 500 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc | LA |  |  | Proposed | 96480929 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 20040 | 25738 | TEQ | 2022-12-31 | All |  |  | 500 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc | LA |  |  | Proposed | 42100000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 20045 | 25744 | Dist | 2024-06-01 | Northline |  |  | 230 |  |  | Northline 230 kV substation will be cut in between the Addis and Cohen 230 kV stations. | LA |  |  | Proposed | 42800000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 |  | Entergy-LA | 20058 | 26098 | RLY | 2022-12-15 | Perryville |  |  | 500 |  |  | Relaying Upgrades at Perryville 500 kV station for Baxter Wilson upgrades | LA |  |  | Proposed | 51846 | [6 empty] | Entergy Mississippi | N | N
A in MTEP21 | South | Entergy-LA | 20122 | 25827 | TEQ | 2021-12-31 | All |  |  | 230 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc | LA |  |  | Proposed | 5900000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 20124 | 25829 | TEQ | 2022-12-31 | All |  |  | 230 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc | LA |  |  | Proposed | 4500000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 20306 | 25997 | RLY | 2021-12-15 | Adams Creek |  |  | 500 |  |  | Relay upgrades at Adams Creek | LA |  |  | Planned | 417756 | [6 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 20307 | 25998 | INT | 2021-03-02 | Par |  |  | 115 |  |  | 115 kV substation constructed between Holton and Franklinton 115 kV substations. | LA |  |  | M5_In Service | 4050923 | [6 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 20585 | 26047 | INT | 2021-03-29 | Vacherie |  |  | 230 |  |  | Facilities required for the interconnection of J1142 at Vacherie 230 kV substation. | LA |  |  | M5_In Service | 4300000 |  |  | Customer funded |  |  |  | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 20628 | 26061 | INT | 2022-12-01 | Vacherie 230 kV |  |  | 230 |  |  | This construction at the existing Vacherie 230 kV substation is to accommodate the interconnection of a solar facility (J1158) | LA |  |  | Proposed | 40000 |  |  | Minimal upgrades required |  |  |  | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 21085 | 26137 | SUB | 2022-12-31 | Sugar House |  |  | 230 |  |  | Entergy is proposing to construct a new 230 kV substation (Sugar House 230 kV Substation) which will serve an industrial customer’s 50 MW of new load in Port Allen, LA. The new lines into the Sugar House substation will be cut in and out (~.7 miles total) of the existing Formosa to Placid 230 kV line. The Sugar House 230 kV station will be constructed as a 3 breaker ring bus. Relocation of a portion of the existing 138 kV line that shares right of way with the 230 kV line will also be part of this project. | LA |  |  | Planned | 20100000 | [6 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 21525 | 26284 | SUB | 2023-06-01 | Sullivan |  |  | 230 |  |  | Cut the Sullivan 230 kV substation into the Southport to Joliet 230 kV line. | LA |  |  | M2a_Pre-Project Approval | 23500000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 |  | Entergy-LA | 21525 | 26322 | LNrc | 2023-06-01 | Southport - ELL portion | Sullivan |  | 230 |  |  | Reconductor the Southport to Sullivan 230 kV line | LA |  |  | M2a_Pre-Project Approval | 2900000 | [6 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-LA | 21525 | 26285 | LNrc | 2023-06-01 | Southport | Sullivan - ENOL portion |  | 230 |  |  | Upgrade the Southport to Sullivan 230 kV line, ENO portion | LA |  |  | M2a_Pre-Project Approval | 700000 |  |  | Costs include in MISO Facility ID 26284 |  |  |  | Entergy | N | N
A in MTEP21 | South | Entergy-MS | 13995 | 23102 | SUB | 2025-06-01 | Tinnin | Catlett |  | 230 |  |  | New 230kV Substation cutting in on the Tinnin to Bozeman 230kV line | MS |  |  | Planned | 32200000 | Planning | [5 empty] | Entergy Mississippi | N | N
A in MTEP21 | South | Entergy-MS | 15848 | 23917 | LNrb | 2024-05-01 | Norfield switching station | Little Creek |  | 115 |  |  | Rebuild L523 (Norfield SS to Little Creek). | MS |  |  | Proposed | 2070000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15848 | 25217 | LINE | 2024-05-01 | Norfield |  |  | 115 |  |  | Entergy - Transmission line adjustments for Norfield and Jayess switching stations. | MS |  |  | Proposed | 3300000 |  |  | Entergy's cost to the project. |  |  |  | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15848 | 23922 | SwSta | 2024-05-01 | Norfield switching station |  |  | 115 |  |  | Build a new 115kV breaker switching station at Norfield. | MS |  |  | Proposed | 2290000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15848 | 23921 | SwSta | 2024-05-01 | Jayess switching station |  |  | 115 |  |  | Build a new 115kV breaker switching station at Jayess. | MS |  |  | Proposed | 1800000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15848 | 23920 | LN | 2024-05-01 | Jayess GOAB | Little Creek GOAB |  | 115 |  |  | Build a new 115kV transmission line from Jayess GOAB to Little Creek GOAB. | MS |  |  | Proposed | 4680000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15848 | 23919 | TAP | 2024-05-01 | Little Creek GOAB |  |  | 115 |  |  | Tap L523 (Norfield SS to Little Creek) with a 115kV GOAB. | MS |  |  | Proposed | 260000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15848 | 23918 | TAP | 2024-05-01 | Jayess GOAB |  |  | 115 |  |  | Tap L549 (Jayess SS to Jayess) with a 115kV GOAB. | MS |  |  | Proposed | 260000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15850 | 23926 | LNrb | 2024-12-01 | Pisgah GOAB | Magee Road switching station |  | 115 |  |  | Rebuild L546 (Pisgah GOAB to Magee Road SS). | MS |  |  | Proposed | 1207500 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15850 | 25218 | LINE | 2024-12-01 | Arlington |  |  | 115 |  |  | Entergy - Transmission line adjustments for Arlington switching station. | MS |  |  | Proposed | 1700000 |  |  | Entergy's cost to the project. |  |  |  | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15850 | 24604 | COM | 2024-12-01 | Magee Road SS | Olive Oil |  | 115 |  |  | Add OPGW to L576 (Magee Road SS - Olive Oil) | MS |  |  | Proposed | 301000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15850 | 23931 | SwSta | 2024-12-01 | Arlington |  |  | 115 |  |  | Build a new 115kV breaker switching station at Arlington. | MS |  |  | Proposed | 1800000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15850 | 23930 | LN | 2024-12-01 | Arlington Sub GOAB | Olive Oil GOAB |  | 115 |  |  | Build a new 115kV transmission line from Arlington Sub GOAB to Olive Oil GOAB. | MS |  |  | Proposed | 4680000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15850 | 23929 | TAP | 2024-12-01 | Olive Oil GOAB |  |  | 115 |  |  | Tap L576 (Magee Road SS to Olive Oil) with a 115kV GOAB. | MS |  |  | Proposed | 260000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15850 | 23928 | TAP | 2024-12-01 | Arlington Sub GOAB |  |  | 115 |  |  | Tap L547 (Arlington GOAB to Arlington) with a 115kV GOAB. | MS |  |  | Proposed | 260000 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 15850 | 23927 | LNrb | 2024-12-01 | Arlington GOAB | Arlington |  | 115 |  |  | Rebuild L547 (Arlington GOAB to Arlington). | MS |  |  | Proposed | 1897500 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | South | Entergy-MS | 20055 | 25757 | RLY | 2023-06-01 | McAdams |  |  | 230 |  |  | Project addresses Relay Single Point of Failure at McAdams 230 kV substation by adding or replacing bus differential protection on the 230kV buses, adding or replacing bus potential transfer panel, replacing two (2) OCBs, breaker control panel and CCVTs. | MS |  |  | Proposed | 4600000 | [6 empty] | Entergy Mississippi | N | N
A in MTEP21 | South | Entergy-MS | 20057 | 25758 | RLY | 2023-06-01 | Lakeover |  |  | 115 |  |  | Install dual primary protection with independent CT and PT winding inputs on the Franklin 115 kV bus. Dual battery installations or monitoring sufficient to meet FERC 754 guidelines. | MS |  |  | Proposed | 1700000 | [6 empty] | Entergy Mississippi | N | N
A in MTEP21 | South | Entergy-MS | 20058 | 25760 | TEQ | 2022-12-15 | Baxter Wilson |  |  | 500 |  |  | Upgrade the following terminal equipment at Baxter Wilson SES SWYD (Perryville Line Bay) to a minimum through-path rating of 1940 MVA: J2217, J2219, Line Trap, SEL321. | MS |  |  | Proposed | 1059079 | [6 empty] | Entergy Mississippi | N | N
A in MTEP21 | South | Entergy-MS | 20060 | 25761 | TEQ | 2021-12-31 | Various - 2021 EML Asset Renewal Program |  |  | 500 | 115 |  | This project includes the EML asset renewal projects that will be performed in 2021. | MS |  |  | Proposed | 29069307 | [6 empty] | Entergy Mississippi | N | N
A in MTEP21 | South | Entergy-MS | 20061 | 25763 | TEQ | 2022-12-31 | Various - 2022 EML Asset Renewal Program |  |  | 500 | 115 |  | This project includes the EML asset renewal projects that will be performed in 2022. | MS |  |  | Proposed | 30477959 | [6 empty] | Entergy Mississippi | N | N
A in MTEP21 | South | Entergy-MS | 20308 | 25999 | RLY | 2021-12-15 | Franklin |  |  | 500 |  |  | Identified by MISO for NRIS/ERIS for the interconnection customers J830, J868 and J908. | MS |  |  | Planned | 900000 | GIA | [5 empty] | Entergy Mississippi | N | N
A in MTEP21 | South | Entergy-TX | 19853 | 25636 | SUB | 2022-12-31 | Fork Creek 138kV |  |  | 138 |  |  | Install (2) 138kV line breakers, install CCVT on line side of breakers, install (3) 138kV bus PTs, install relay panels in existing control house. | TX |  |  | Planned | 900000 | Planning Preliminary | [5 empty] | East Texas Electric Cooperative Inc. | N | N
A in MTEP21 | South | Entergy-TX | 19954 | 25663 | SUB | 2023-04-01 | Jasper Newton 69 kV |  |  | 138 | 69 |  | Route Entergy 138 kV line #420 in and out of adjacent JNEC Newton 69 kV substation. At JNEC Newton, install 138/69 kV transformer and 138 kV line breakers and relaying. | TX |  |  | Planned | 3800000 | Planning Preliminary | [5 empty] | East Texas Electric Cooperative Inc. | N | N
A in MTEP21 |  | Entergy-TX | 19954 | 25664 | BUS | 2023-04-01 | Jasper Newton 69 kV |  |  | 138 | 69 |  | At JNEC Newton, install 138 kV bus. | TX |  |  | Planned | 1500000 | Planning Preliminary | [5 empty] | East Texas Electric Cooperative Inc. | N | N
A in MTEP21 | South | Entergy-TX | 20042 | 25739 | TEQ | 2021-12-31 | All |  |  | 500 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc | TX |  |  | Proposed | 22100000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-TX | 20043 | 25740 | TEQ | 2022-12-31 | All |  |  | 500 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc | TX |  |  | Proposed | 32500000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-TX | 20067 | 25770 | Dist | 2023-12-01 | Southline |  |  | 138 |  |  | Southline 138 kV distribution station will be cut into the Cleveland to Jayhawker 138 kV line. | TX |  |  | Proposed | 34800000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-TX | 20073 | 25772 | TX | 2024-06-01 | Ponderosa |  |  | 230 |  |  | Install a power transformer at Ponderosa 230 kV | TX |  |  | Proposed | 23500000 | Planning | [5 empty] | Entergy | N | N
A in MTEP21 | South | Entergy-TX | 20405 | 26028 | INT | 2023-01-01 | Poco | Menard |  | 138 |  |  | This project is to construct the interconnection station for the solar project J1030 on the Poco to Menard 138 kV line. | TX |  |  | Proposed | 7150200 | Planning |  | estimate from GIA |  |  |  | Entergy | N | N
A in MTEP21 | Central | GLH | 19746 | 25560 | LNrb | 2022-03-01 | Joppa | Shawnee | 2 | 161 |  |  | Rebuild 6.4 miles of 161 kV line Joppa- Shawnee ckt 2. | IL,KY | 6.4 |  | Planned | 11000000 | Budgetary | 2020 |  |  |  |  | Gridliance | N | N
A in MTEP21 | Central | GLH | 20001 | 25678 | LNrb | 2023-06-01 | Joppa | Shawnee | 3 | 161 |  | 330 | Rebuild Joppa-Shawnee 161 kV Ckt 3 | IL,KY | 8 |  | Planned | 11700000 | Planning | 2021 |  | 391 |  |  | Gridliance | N | N
A in MTEP21 | Central | GLH | 20004 | 25680 | LNrb | 2023-06-01 | Joppa | Shawnee | 4 | 161 |  |  | Rebuild 8 miles of Joppa-Shawnee 161 kV Ckt 4 | IL,KY | 8 |  | Planned | 11700000 | Planning | 2021 |  |  |  |  | Gridliance | N | N
A in MTEP21 | Central | GLH | 20005 | 25681 | LNrb | 2023-06-01 | Joppa | Shawnee | 1 | 161 |  |  | Rebuild Joppa - Shawnee 161 kV ckt 1 | KY,IL | 10 |  | Planned | 14700000 | Planning | 2021 |  |  |  |  | Gridliance | N | N
A in MTEP21 |  | GRE | 17996 | 25912 | BUS | 2022-07-19 | Willmar |  |  | 115 |  |  | Remove existing box structure and install 115kV bus work associated with the Priam outlet position including transformer low side switch, line breaker and disconnects, and all associated foundations, control cable and protection and control equipment. 115kV will be laid out for future ring bus configuration. | MN |  |  | Proposed | 5740643.31 | Planning | 2020 |  |  |  |  | Great River Energy | N | N
A in MTEP21 | West | GRE | 18865 | 25331 | LNrc | 2021-07-10 | Square Butte | Stanton | 1 | 230 |  |  | Upgrade Square Butte - Stanton 230 kV line | ND | 16 |  | Proposed | 6379446 | Planning Preliminary | 2019 |  |  |  |  | Great River Energy | N | N
A in MTEP21 | West | GRE | 20139 | 25844 | LNrb | 2024-05-01 | Winthrop McLeod | Winthrop Xcel | 1 | 69 |  |  | Rebuild MC-WW (9 miles) to upgradable 69kV with T2 capable of 1500-1600 amps. Remove SS2950 Winthrop tap switch. | MN | 9 |  | Proposed | 6616829 | Planning | 2020 |  |  |  |  | Great River Energy | N | N
A in MTEP21 | West | GRE | 20141 | 25847 | LNrb | 2023-10-27 | Decoria | Stoney Creek | 1 | 69 |  |  | Rebuild BE-MD segments 1 and 2 (4.02 miles) and SS2826 to 69kV with T2 1200 amp capable conductor. | MN | 4.02 |  | Proposed | 3015848.74 | Planning | 2020 |  |  |  |  | Great River Energy | N | N
A in MTEP21 | West | GRE | 20143 | 25852 | SwSta | 2022-08-26 | Wing River |  |  | 230 |  |  | Convert the 230 kV portion of the Wing River substation into a ring bus. | MN |  |  | Proposed | 3247667.74 | Planning | 2020 |  |  |  |  | Great River Energy | N | N
A in MTEP21 | West | GRE | 20148 | 25853 | LN | 2026-07-31 | Appleton | Benson | 1 | 115 |  |  | Construct about 27 miles of 115 kV transmission line from Appleton to GRE’s AG-BK line and about 1.75-mile 115 kV transmission line from AG-BK line to Benson Muni substation with associated tap switch, distribution sub, and retirement projects. | MN |  | 26 | Proposed | 26773673 | Planning | 2020 |  |  |  |  | Great River Energy | N | N
A in MTEP21 | West | GRE | 20151 | 25858 | SwSta | 2021-12-31 | Milaca |  |  | 69 |  |  | Move ECE’s Milaca delivery points from the auxiliary bus onto the main bus and with circuit breaker protection. | MN |  |  | Proposed | 419407.71 | Planning | 2020 |  |  |  |  | Great River Energy | N | N
A in MTEP21 | West | GRE, MRES | 20608 | 26074 | SUB | 2022-11-01 | New Worthington Sub |  |  | 69 |  |  | This includes all of the 69 kV buswork, breakers, and capacitor bank additions at the New Worthington substation. Preliminary designs of the 69 kV bus include two breakers for the GRE line interconnection, and two breakers for a two-stage capacitor bank (2 x 7.0 MVAR). | MN |  |  | M3_Long Lead Materials | 4800000 | Engineering Preliminary | [5 empty] | Missouri River Energy Services (MRET) | N | N
A in MTEP21 | Central | IPL | 20134 | 25840 | SUB | 2022-12-31 | Stout |  |  | 345 |  |  | One 345 kV Breaker | IN |  |  | Planned | 3150400 | Planning | [5 empty] | Indianapolis Power & Light Company | N | N
A in MTEP21 | Central | IPL | 20137 | 25843 | SUB | 2023-12-31 | Guion |  |  | 345 | 138 |  | One (1) new third 500 MVA auto transformer is scheduled to be installed at Guion substation. The project includes three (3) new 345 kV breakers, two (2) replacement 345kV breakers, two (2) 138 kV breakers, and terminal equipment including disconnect switches, relays, etc. | IN |  |  | Planned | 13376000 | Planning | [5 empty] | Indianapolis Power & Light Company | N | N
A in MTEP21 | West | ITCM | 17968 | 24735 | SUB | 2023-05-31 | Thisius | Substation |  | 161 | 69 |  | ITC will install the 100MVA 161:69kV transformer from Glenworth at Thisius once it is replaced in an unrelated GI project. The 161kV will be built to a ring bus while the 69kV will be built to a straight bus using a single box structure. All 161kV equipment will have a 2000A minimum and new 69kV equipment will be good for 1200A minimum. | MN |  |  | Planned | 7168877 | Engineering Preliminary | 2019 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 17968 | 24737 | TAP | 2023-05-31 | Huntley | Walters | 1 | 69 | 69 |  | Tap the Huntley – Walters 69kV circuit and route it into the new substation using T2-477 ACSR. | MN |  |  | Planned | 300000 | Engineering Preliminary | 2019 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 17968 | 24736 | TAP | 2023-05-31 | Freeborn | Huntley | 1 | 161 | 161 |  | Tap the Freeborn – Huntley 161kV circuit and route it into the new substation using T2-795 ACSR. | MN |  |  | Planned | 420000 | Engineering Preliminary | 2019 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 19925 | 25607 | LN | 2024-12-31 | Albia | Melrose | 1 | 69 | 69 |  | The majority of the Albia to Melrose 69kV line is near end of life and in poor condition. The line between the Albia and Melrose substations (~17.25 miles) will be rebuilt to current 69kV standards. All new equipment should be rated at 600A or higher minimum summer normal rating. | IA | 17.25 |  | Planned | 16293244 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 19926 | 25608 | LNrb | 2024-12-31 | Osceola North | Osceola REC | 1 | 69 | 69 |  | Osceola N-Woodburn Jct 69kV Rebuild | IA | 3.99 |  | Planned | 4248000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 19926 | 25609 | LNrb | 2024-12-31 | Osceola REC | Woodburn Jct | 1 | 69 | 69 |  | The majority of the Osceola North to Woodburn 69kV line is near end of life and in poor condition. The line between the Osceola North, Osceola Rec, and Woodburn Jct. substations (~9.57 miles) will be rebuilt to current 69kV standards. All new equipment should be rated at 600A or higher minimum summer normal rating. | IA | 5.58 |  | Planned | 4716000 | Engineering Preliminary | 2020 | This line section was submitted & approved in MTEP12 in project 3643. ITCM will withdraw project 3643 upon approval of this project in MTEP21. |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 19928 | 25611 | SUB | 2025-12-31 | Old Settlers | 115kV Bus K1 |  | 115 | 115 |  | ITC will install an additional 115kV breaker on Bus K1 at Old Settlers. All new terminal equipment will be capable of 2000A minimum. | IA |  |  | Planned | 878438 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 19928 | 25616 | TAP | 2025-12-31 | Dry Creek | Old Settlers |  | 115 | 115 |  | Reterminate Dry Creek - Old Settlers 115kV circuit into new position at Old Settlers using T2-477 | IA |  |  | Planned | 336000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 19928 | 25615 | TAP | 2025-12-31 | Marion | Old Settlers |  | 115 | 115 |  | ITC will rebuild the existing ~0.5 mi tap into Old Settlers double circuit with T2-477. These circuits will be terminated into the new positions at Marion and Old Settlers using T2-477. | IA | 0.5 |  | Planned | 1890000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 19928 | 25612 | SUB | 2025-12-31 | Marion | 115kV Bus K2 |  | 115 | 115 |  | ITC will install an additional 115kV breaker on Bus K2 at Marion. All new terminal equipment will be capable of 2000A minimum. | IA |  |  | Planned | 1128140 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 19931 | 25617 | LNup | 2022-12-31 | Dickinson County | Triboji | 1 | 161 | 161 |  | Remove all existing sag limits on Dickinson County – Triboji 161 kV line to raise 636 ACSR to full summer conductor rating at 212 F (953/953/953 amps SN/SE/SSE 266/266/266 MVA SN/SE/SSE). | IA |  |  | Planned | 369600 | Engineering | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 19993 | 25667 | CAP | 2023-12-31 | Triboji | Capacitor |  | 69 | 69 | 11.25 MVAR | ITC will install a 11.25MVAR Effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor on the Triboji J2 bus. All new substation equipment should have a minimum rating of 1200A. | IA |  |  | Planned | 813960 | Engineering | 2020 |  | 11.25 MVAR |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 19995 | 25670 | CAP | 2023-12-31 | West Union | Capacitor |  | 69 | 69 | 11.25 MVAR | ITC will install a 11.25MVAR Effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor on the West Union J2 bus. All substation equipment should have a minimum rating of 1200A. | IA |  |  | Planned | 812280 | Engineering | 2020 |  | 11.25 MVAR |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 19996 | 25671 | SUB | 2023-12-31 | Monona | Substation |  | 69 | 69 | 11.25 MVAR | ITC rebuild the Monona 69kV substation and install a 11.25MVAR Effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor at a new Monona Substation adjacent to the existing site. All substation equipment should have a minimum rating of 1200A. | IA |  |  | Planned |  |  |  |  | 11.25 MVAR |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 19996 | 26091 | LN | 2022-12-31 | Monona | IPL dist customer | 1 | 69 | 69 |  | Radial line to IPL distribution customer. | IA |  |  | Planned | 48000 | Engineering | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 19996 | 26090 | LN | 2022-12-31 | Monona | Ckt 432 | 1 | 69 | 69 |  | Monona Circuit 432 line work | IA |  |  | Planned | 246000 | Planning | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 19996 | 26089 | LN | 2022-12-31 | Monona | Turkey River | 1 | 69 | 69 |  | Monona-Turkey River line work | IA |  |  | Planned | 312000 | Engineering | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 19996 | 26088 | LN | 2022-12-31 | Monona | Lansing | 1 | 69 | 69 |  | Monona-Lansing line work | IA |  |  | Planned | 330000 | Engineering | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 19996 | 26087 | LN | 2022-12-31 | Monona | Postville | 1 | 69 | 69 |  | Monona-Postville line work | IA |  |  | Planned | 216000 | Engineering | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 20025 | 25714 | LNrb | 2024-12-31 | Bethel | Tripoli | 1 | 69 | 69 |  | The line between the Bethel substation and Fredericksburg Tap (~8 miles) will be rebuilt to current 69kV standards. All new equipment should be rated 600A or higher minimum summer normal rating. | IA | 8 |  | Planned | 7740000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 20026 | 25715 | LNrb | 2024-12-31 | Osage Jct | Douglas Tap | 1 | 69 | 69 |  | Phase 1: The line between Osage JCT and Douglas Tap (~13.9 miles) will be rebuilt to current 69kV standards. All new line equipment should be rated 600A or higher. | IA | 13.9 |  | Planned | 12660000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 20026 | 25716 | LNrb | 2024-12-31 | Riceville | Rice | 1 | 69 | 69 |  | Phase 2: The line between Riceville and Rice (~9.8 miles) will be rebuilt to current 69kV standards. All new line equipment should be rated 600A or higher. | IA | 9.8 |  | Planned | 10320000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 20027 | 25717 | Remove | 2022-12-31 | Meservey | 69kV Tap | 1 | 69 | 69 |  | Retire ~6.9 miles of 69kV line to the IPL owned Meservey substation. Also remove line switches 4122 and 4123. All poles with underbuild should be topped per underbuild owner specification. All necessary outages should be coordinated with IPL. | IA | 6.9 |  | Planned | 420000 | Engineering | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 20028 | 25718 | LNrb | 2024-12-31 | Emery | 6th Ave | 1 | 69 | 69 |  | Beginning at where the double circuit ends (~0.35 miles outside Emery) - IPL’s 6th Ave substation will be rebuilt (~5.54 miles of line) to current 69kV standards. All new line should be rated 1200A or higher. | IA | 5.54 |  | Planned | 7200000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 20029 | 25720 | LN | 2026-05-01 | Winterset Jct | Tiberius | 1 | 161 | 161 | 2000 amps | ITC will be building about 29 miles of 161kV line from CIPCO’s Winterset Jct. to Osceola’s new substation. All new lines should be T2 636 ACSR and rated at 2000A or higher minimum summer normal rating. | IA |  | 29 | Planned | 49647695 | Engineering Preliminary | 2020 |  | 2000 amps |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 20029 | 25730 | TAP | 2026-05-01 | Lenox | Lenox Tap | 1 | 69 | 69 |  | ITC will be building a new breaker station at the “Lenox Tap” position. This station will replace the 3-way switch currently in use and connect our Lenox line and substation (IPL owned) to the new 69kV transmission system being built by CIPCO from the northwest (Corning/Brooks). All new 69kV equipment will need to be rated for 1200A minimum summer normal rating. | IA |  |  | Planned | 327863 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 20029 | 25728 | TAP | 2026-05-01 | Creston | Mount Ayr | 1 | 69 | 69 |  | ITC will be building a new breaker station at the “Lenox Tap” position. This station will replace the 3-way switch currently in use and connect our Lenox line and substation (IPL owned) to the new 69kV transmission system being built by CIPCO from the northwest (Corning/Brooks). All new 69kV equipment will need to be rated for 1200A minimum summer normal rating. | IA |  |  | Planned | 461779 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 20029 | 25727 | TAP | 2026-05-01 | Bridgeport North | Centerville North | 1 | 69 | 69 |  | ITC will be building a new breaker station northeast of the Albia substation. This station will connect the 69kV line from Albia to Court and the 69kV line from Bridgeport to Centerville. Since the two lines have an intersection point (about 1.5 miles NE of the Albia sub), minimal line construction will be needed. | IA |  |  | Planned | 453174 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 20029 | 25726 | TAP | 2026-05-01 | Albia | Court | 1 | 69 | 69 |  | ITC will be building a new breaker station northeast of the Albia substation. This station will connect the 69kV line from Albia to Court and the 69kV line from Bridgeport to Centerville. Since the two lines have an intersection point (about 1.5 miles NE of the Albia sub), minimal line construction will be needed. | IA |  |  | Planned | 453174 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 20029 | 25724 | LN | 2026-05-01 | Lenox | Lenox Muni | 1 | 69 | 69 |  | ITC will be installing a 2-way switch outside IPL’s Lenox substation, building a new 69kV line (about 2.6 miles), and connecting it into CIPCO’s substation “Lenox Muni”. | IA |  | 2.6 | Planned | 3899124 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 20029 | 25723 | SwSta | 2026-05-01 | Golem | Substation |  | 69 | 69 |  | New 69kV breaker station in the Lenox area. | IA |  |  | Planned | 3295682 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 20029 | 25722 | SwSta | 2026-05-01 | Raysh | Substation |  | 69 | 69 |  | New 69kV switch station in the Albia area. | IA |  |  | Planned | 4359745 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 20029 | 25721 | SUB | 2026-05-01 | Tiberius | Substation |  | 161 | 69 | 150 MVA | ITC will construct a new Tiberius 161/69kV, 150 MVA transformer will be needed in the Osceola area to provide a new 69kV source for the area. | IA |  |  | Planned | 8311951 | Engineering Preliminary | 2020 |  | 150 MVA |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 20035 | 25733 | CAP | 2022-07-01 | Hickory Creek | Capacitor |  | 345 | 345 | 2 x 84MVAR | The MPFCA provides for ITC Midwest to fund the cost of 2 x 84 MVAR (rated) capacitor banks at the Hickory Creek 345 kV substation. | IA |  |  | Planned | 7355598 | Engineering | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 |  | ITCM | 20035 | 25734 | CAP | 2022-07-01 | Killdeer | Capacitor |  | 345 | 345 | 2 x 84MVAR | The MPFCA provides for ITC Midwest to fund the cost of 2 x 84 MVAR (rated) capacitor banks at Killdeer 345 kV substation and 2 x 84 MVAR capacitor banks at Hickory Creek 345 kV substation. | IA |  |  | Planned | 8742263 | Engineering | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 20037 | 25736 | LNrb | 2024-12-31 | Carbide | Viele | 1 | 161 | 161 |  | ITC Midwest has entered into an agreement with Northeast Missouri Electric Cooperative to rebuild approximately 12.3 miles of the ITC Carbide – Viele 161 kV line to double circuit to allow Northeast to connect a new 161 kV line from their Franklin Substation in Lee County, Iowa to their Winchester Substation in Clarke County, Missouri. Per the terms of the agreement, Northeast will be responsible for design and construction for this project. ITC will contribute a fixed amount of $6,120,00 for the project as a credit for planned maintenance ITC needs to perform on this line. The ITC portion of the rebuild will be constructed with T2-795 ACSR conductor and OPGW. ITC will own the double circuit poles, conductor, insulators, and 1 OPGW static wire. | IA | 12.3 |  | Planned | 6200000 | Engineering | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 20180 | 25940 | LN | 2024-12-31 | Blanket for Customer Interconnections under $1 million for 2024 | Throughout system |  | 345 | 69 |  | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL |  |  | Planned | 2400000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 21429 | 26263 | SUB | 2022-12-31 | Tiffin Crossroads | Substation |  | 69 | 69 | 20 MVA | IPL will be building a new 69/25x12.5 kV substation named “Tiffin Crossroads” adjacent to the existing MidAmerican Tiffin Sub K substation. This new substation will replace the existing IPL Tiffin distribution substation and accommodate future area load growth. IPL will be installing one 12/20 MVA transformer initially but is planning the substation to accommodate a 2nd 12/20 MVA transformer in the future. For the ITC owned portion of Tiffin Crossroads, ITC will build a new 69 kV substation with two single boxes, two line breakers, and a bus tie breaker. | IA |  |  | Planned | 3982070 | Engineering | 2021 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 21429 | 26265 | SUBmisc | 2022-12-31 | Tiffin Sub K | Substation |  | 69 | 69 |  | Make necessary relay and communication upgrades at Tiffin Sub K to accommodate new Crossroads substation. | IA |  |  | Planned | 43598 | Engineering | 2021 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 21429 | 26264 | LN | 2022-12-31 | Tiffin Crossroads | Sub K Tiffin |  | 69 | 69 |  | Line taps for the new Tiffin Crossroads substation. | IA |  |  | Planned | 1106740 | Engineering | 2021 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 21625 | 26302 | SUB | 2022-10-30 | Keokuk Geode | Substation |  | 69 | 69 |  | IPL will be building a new 69/25x12.5 kV Substation named Keokuk Geode. The new Keokuk Geode Substation will replace the Messenger Substation and Commercial Substation. IPL will be installing one 69/24.9x12.5 kV 20/33MVA transformer initially but is planning the substation to accommodate a second 69/24.9x12.5 kV transformer when all the load is transferred from the Messenger Substation and Commercial Substation. | IA |  |  | Planned | 4128418 | Engineering | 2021 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM | 21625 | 26303 | LN | 2022-10-30 | Carbide | Messenger | 1 | 69 | 69 |  | New line route to the Keokuk Geode 69 kV Substation | IA |  |  | Planned | 636000 | Engineering | 2021 |  |  |  |  | ITC Midwest | N | N
A in MTEP21 | West | ITCM, MEC | 20685 | 26065 | SwSta | 2020-04-01 | Gard Ave |  |  | 345 |  |  | New switching station | IA |  |  | Proposed | 11500000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | ITCM, MEC | 20685 | 26066 | TAP | 2020-04-01 | Gard Ave | Lehigh |  | 345 |  |  | Add taps | IA |  |  | Proposed | 1200000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | East | ITCT | 18237 | 25064 | SUB | 2023-12-31 | Various |  |  | 345 | 120 |  | Replace aging and outdated equipment at a pace that will insure each type of equipment is replaced near its projected end of life. | MI |  |  | Proposed | 34200000 | Budgetary | 2020 | Equipment includes line and station equipment |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19185 | 25415 | SUB | 2023-12-31 | Red Run |  |  | 230 |  |  | Install a 230kV line breaker at Red Run | MI |  |  | Proposed | 1500000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19185 | 25416 | SUB | 2023-12-31 | Bismarck |  |  | 230 |  |  | Install a 230kV line breaker at Bismarck | MI |  |  | Proposed | 1200000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19266 | 25445 | SUB | 2022-03-31 | J799 Interconnection |  |  | 120 |  |  | J799 Interconnection 120kV is a ring bus station with 3 40kA breakers. | MI |  |  | M2a_Pre-Project Approval | 5610000 | Engineering | 2019 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19266 | 25447 | SUBmisc | 2022-03-31 | Milan |  |  | 120 |  |  | Upgrade SCADA and relaying equipment at Milan 120kV to support new J799 Interconnection. | MI |  |  | M2a_Pre-Project Approval | 280000 | Engineering | 2019 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19266 | 25446 | LN | 2022-03-31 | Milan | Pioneer | 1 | 120 |  |  | Extend the Milan - Pioneer 120kV line 0.2 miles to loop in the J799 Interconnection station for transmission service. | MI |  | 0.2 | M2a_Pre-Project Approval | 1630000 | Engineering | 2019 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19405 | 25470 | SUB | 2022-04-29 | J833 Interconnection |  |  | 120 |  |  | Construct the J833 Interconnection 120kV station with three 40kA breakers. | MI |  |  | M2a_Pre-Project Approval | 5760000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19405 | 25472 | RLY | 2022-04-29 | Pioneer |  |  | 120 |  |  | Upgrade Pioneer 120kV relaying and SCADA equipment | MI |  |  | M2a_Pre-Project Approval | 560000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19405 | 25471 | LN | 2022-04-29 | Milan | Pioneer |  | 120 |  |  | Extend the Milan - Pioneer 120kV line by adding 0.5 miles of 954 ACSR to loop in the J833 Interconnection station for transmission service | MI |  |  | M2a_Pre-Project Approval | 3970000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19508 | 25497 | LINE | 2021-12-31 | Bauer | Pontiac |  | 345 |  |  | Remediate the sag on the Bauer - Pontiac 345kV circuit, conductor type 2156 ACSR, to achieve a minimum rating of 2573 Amps summer emergency. Remediate the sag on the Bauer - Pontiac 345kV circuit, conductor type 2-954 ACSR, to achieve a minimum rating of 2573 Amps summer emergency. | MI |  |  | M2a_Pre-Project Approval | 7103000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19508 | 25498 | SUB | 2021-12-31 | Pontiac |  |  | 345 |  |  | Replace Pontiac 345kV switches DV, DR, DO, and DK to achieve a minimum rating of 1537 MVA summer emergency. | MI |  |  | M2a_Pre-Project Approval | 1106000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19509 | 25499 | LINE | 2021-12-31 | Thetford | Jewell |  | 345 |  |  | Reconductor approximately 0.1 miles of the Thetford – Jewell 345kV circuit with a conductor rated at least that of 2-945 ACSR. Remediate the sag on the Thetford - Jewell 345kV circuit to achieve a minimum rating of minimum summer emergency circuit rating of 1556 MVA. | MI |  |  | M2a_Pre-Project Approval | 5662000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19585 | 25512 | LNup | 2021-12-31 | Placid | Pontiac |  | 345 |  |  | Remediate the sag on the Placid – Pontiac 345kV circuit to achieve the minimum rating required to interconnect associated generators as studied in DPP-2017-Aug | MI |  |  | M2a_Pre-Project Approval | 2956000 | Engineering | 2019 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19586 | 25513 | LNup | 2021-12-31 | Pontiac | Wixom |  | 345 |  |  | Raise the sag limit on Pontiac-Wixom 345 kV circuit to the minimum rating requried to interconnect associated generators. | MI |  |  | M2a_Pre-Project Approval | 1015000 | Engineering | 2019 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19586 | 25515 | SUBmisc | 2021-12-31 | Wixom |  |  | 345 |  |  | Upgrade Wixom 345kV switch DD. Upgrade Wixom 345kV wave trap at position DI. | MI |  |  | M2a_Pre-Project Approval | 291000 | Engineering | 2019 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19586 | 25514 | SUBmisc | 2021-12-31 | Pontiac |  |  | 345 |  |  | Upgrade Pontiac 345kV switches BD, BH, BK, BO and associated buswork. Upgrade Pontiac 345kV thermal relay at position BI. | MI |  |  | M2a_Pre-Project Approval | 1176000 | Engineering | 2019 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 19992 | 25666 | TEQ | 2022-12-31 | Throughout System |  |  | 120 |  |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | MI |  |  | Proposed | 1000000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20036 | 25750 | SUB | 2024-06-01 | Sebewaing |  |  | 345 | 120 |  | Construct New Sebewaing Station as a 345kV - 120kV station with three 345kV 40kA breakers and one 120kV 40kA breaker. Install a 345/120kV transformer. | MI |  |  | Proposed | 19900000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 |  | ITCT | 20036 | 26099 | RLY | 2024-06-01 | Rapson |  |  | 345 |  |  | Upgrade Relaying | MI |  |  | Proposed | 75000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 |  | ITCT | 20036 | 26033 | SUBmisc | 2024-06-01 | Stein |  |  | 345 |  |  | Install Fiber Jumpers | MI |  |  | Proposed | 43000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 |  | ITCT | 20036 | 26032 | SUBmisc | 2024-06-01 | Ringle |  |  | 345 |  |  | Install Fiber Jumpers | MI |  |  | Proposed | 43000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 |  | ITCT | 20036 | 26031 | SUBmisc | 2024-06-01 | Kirk |  |  | 345 |  |  | Install Fiber Jumpers | MI |  |  | Proposed | 43000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 |  | ITCT | 20036 | 26030 | RLY | 2024-06-01 | Grassmere |  |  | 345 |  |  | Upgrade Position AQ relaying | MI |  |  | Proposed | 165000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 |  | ITCT | 20036 | 26029 | RLY | 2024-06-01 | Bauer |  |  | 345 |  |  | Upgrade Position EQ relaying | MI |  |  | Proposed | 75000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20036 | 25752 | LN | 2024-06-01 | Sebewaing | Sebewaing |  | 120 |  |  | Install 4.5 miles of 954 ACSR in new right of way to connect Sebewaing's new station to ITC's Sebewaing 120kV at position HQ. | MI |  |  | Proposed | 11100000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20036 | 25751 | LN | 2024-06-01 | Bauer | Grassmere |  | 345 |  |  | Extend the Bauer - Grassmere 345kV line by adding 0.2 miles of 954 ACSR to loop in Sebewaing 345kV for transmission service. | MI |  |  | Proposed | 1100000 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20044 | 25742 | SUBmisc | 2024-12-31 | Blanket for Customer Interconnections | Throughout System |  | 120 |  |  | Blanket for customer interconnections and retirements less than $1 million with in service date in the year 2024 | MI |  |  | Proposed | 2000000 | Budgetary | [5 empty] | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20107 | 25807 | SUB | 2024-12-31 | Atlanta |  |  | 138 | 120 |  | Add HG, GB,GF brkrs and switches | MI |  |  | Proposed | 4100000 | Engineering | [5 empty] | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20107 | 25808 | LNrb | 2024-12-31 | Atlanta | Karn/Thetford | 1 | 138 |  |  | Rebuild 0.75 miles utilizing 1431 ACSR on standard double circuit structures | MI |  |  | Proposed | 1300000 | Engineering | [5 empty] | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20132 | 25838 | TX | 2025-12-31 | Pontiac |  |  | 345 | 120 |  | Replace Pontiac 303 345/120kV Transformer. | MI |  |  | Proposed | 4800000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20133 | 25839 | TX | 2025-12-31 | Hines |  |  | 230 | 120 |  | Replace the Hines 201 230/120kV transformer | MI |  |  | Proposed | 4800000 | Engineering Preliminary | [5 empty] | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20138 | 25842 | TX | 2023-12-31 | Milan |  |  | 345 | 120 |  | Replace the Milan #303 345/120kV transformer | MI |  |  | Proposed | 4800000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20140 | 25846 | TX | 2023-12-31 | Pontiac |  |  | 345 | 120 |  | Replace the Pontiac #301 345/120kV transformer | MI |  |  | Proposed | 4800000 | Engineering Preliminary | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20167 | 25898 | LN | 2024-12-31 | Cato | Corktown | 1 | 120 |  |  | Build approximately 0.85 miles of 120kV 1600mm² underground cable from Cato to Corktown. Include underground direct fiber through conduit | MI |  | 0.85 | Proposed | 17000000 | Engineering | [5 empty] | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20167 | 25901 | SwSta | 2024-12-31 | Cato |  |  | 120 |  |  | Upgrade Cato to a 4 breaker ring bus to accommodate a third line termination. Install 3 standard 3000A breakers, associated disconnect switches and line switches. All breakers at Cato to have interrupting capability of at least 50kA | MI |  |  | Proposed | 14800000 | [6 empty] | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20167 | 25900 | SwSta | 2024-12-31 | Corktown |  |  | 120 |  |  | Install bus 104, standard 3000A breakers JC and HT, and associated disconnects and line switch. All breakers at Corktown to have interrupting capability of at least 50kA | MI |  |  | Proposed | 8200000 | Engineering | [5 empty] | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20325 | 26001 | LNrl | 2022-12-31 | Custer | Monroe | 1 | 120 |  |  | Relocate approximately 1 mile of 120kV circuit | MI | 1.8 |  | Proposed | 8800000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 20845 | 26105 | LNrl | 2023-12-31 | Apache | Seneca | 1 | 120 |  |  | Relocate 9 structures of the Apache-Seneca 120kV circuit along Rochester Road in the city of Troy | MI |  |  | Planned | 2040000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21026 | 26129 | LNrl | 2022-12-31 | Catalina | Montcalm | 1 | 120 |  |  | Bypass Montcalm Station | MI |  |  | Planned | 350000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21026 | 26132 | SwSta | 2022-12-31 | Walton |  |  | 120 |  |  | Relay Upgrades to bypass Montcalm | MI |  |  | Planned | 340000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21026 | 26131 | SwSta | 2022-12-31 | Catalina |  |  | 120 |  |  | Relay upgrades to bypass Montcalm | MI |  |  | Planned | 170000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21026 | 26130 | SUB | 2022-12-31 | Montcalm |  |  | 120 |  |  | Retire station and remove assets | MI |  |  | Planned | 780000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21047 | 26135 | IND | 2023-12-31 | Waterman |  |  | 120 |  |  | Replace Waterman 120kV series reactor HX with a new reactor | MI |  |  | Proposed | 900000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21105 | 26138 | LN | 2023-05-28 | Hunters Creek | Lapeer |  | 120 |  |  | Cut in the ITCT Hunters Creek-Lapeer line to the new in-and-out station. | MI |  | 4 | M2a_Pre-Project Approval | 12446400 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21105 | 26141 | SwSta | 2023-05-28 | Apollo |  |  | 120 |  |  | Construct a new in-and-out station. Install one 120 kV tie breaker, two 120 kV line breakers, buswork, and associated disconnects. | MI |  |  | M2a_Pre-Project Approval | 4068682 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21105 | 26140 | RLY | 2023-05-28 | Hunters Creek |  |  | 120 |  |  | Upgrade remote end protection and control at Lapeer. | MI |  |  | M2a_Pre-Project Approval | 330632 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21105 | 26139 | RLY | 2023-05-28 | Lapeer |  |  | 120 |  |  | Upgrade remote end protection and control at Lapeer. | MI |  |  | M2a_Pre-Project Approval | 301538 | Engineering | 2020 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21170 | 26168 | SUB | 2023-06-01 | Shrine |  |  | 120 |  |  | Construct a new 120kV station with two 40kA line breakers and one 40kA section breaker. | MI |  |  | M2a_Pre-Project Approval | 4275432 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21170 | 26175 | LNup | 2023-06-01 | Bismarck | Golf |  | 120 |  |  | install fiber from the new station to Bismarck along the Bismarck - Golf line | MI | 4.5 |  | M2a_Pre-Project Approval | 3318000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21170 | 26174 | SUBmisc | 2023-06-01 | Sigma |  |  | 120 |  |  | Install fiber patch | MI |  |  | M2a_Pre-Project Approval | 13592 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21170 | 26173 | SUBmisc | 2023-06-01 | Jewell |  |  | 345 |  |  | Install fiber patch panels | MI |  |  | M2a_Pre-Project Approval | 13592 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21170 | 26172 | SUBmisc | 2023-06-01 | Bismarck |  |  | 345 |  |  | Install Fiber patch Panels | MI |  |  | M2a_Pre-Project Approval | 140244 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21170 | 26171 | RLY | 2023-06-01 | Stephens |  |  | 120 |  |  | Upgrade Stephens position HS relaying | MI |  |  | M2a_Pre-Project Approval | 447240 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21170 | 26170 | RLY | 2023-06-01 | Lenox |  |  | 120 |  |  | Upgrade Lenox position HS relaying. | MI |  |  | M2a_Pre-Project Approval | 324612 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21170 | 26169 | LN | 2023-06-01 | Lenox | Stephens |  | 120 |  |  | Extend the Lenox - Stephens 120kV line by adding about 1 mile of 954 ACSR DCT to loop in the new station. | MI |  | 2 | M2a_Pre-Project Approval | 6031200 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21206 | 26180 | LNup | 2023-12-31 | Coventry | Nitro | 1 | 120 |  |  | Disconnect the 954 ACSR conductor running north from the Baltic Tap and connect it to the 1431 ACSR conductor on the north side of the structures heading toward Coventry 120 kV and install Fiber. Also, Remediate sag from Coventry to the Nitro cut-in to a target rating of 269 MVA SE (233F, 1295 A). | MI |  |  | Proposed | 2250000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21206 | 26184 | SUB | 2023-12-31 | Hager |  |  | 120 |  |  | Terminate new line into position HI at Hager 120 kV with a standard 3000 A, 40 kA line breaker and associated standard 3000 A disconnect | MI |  |  | Proposed | 1500000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21206 | 26183 | SUB | 2023-12-31 | Duvall |  |  | 120 |  |  | Install standard 3000 A, 40 kA section breaker and Replace line switches with 3000 A 120 kV load breaking disconnects | MI |  |  | Proposed | 1050000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21206 | 26182 | SUB | 2023-12-31 | Coventry |  |  | 120 |  |  | Terminate the new 120 V line from Nitro into open GJ at Coventry 120 kV. All associated equipment will be standard 3000 A 120 kV. Breaker will be rated at 63 kA | MI |  |  | Proposed | 905000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21206 | 26181 | LNrb | 2023-12-31 | Duval Tap | Hager | 1 | 120 |  |  | Rebuild approximately 1 mile from Duvall tap to Hager utilizing 954 ACSR conductor on standard double circuit steel pole 120 kV structures. Install OPGW on Hager – Hines & Hager – Duvall circuits | MI | 1 |  | Proposed | 5250000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | East | ITCT | 21626 | 26304 | RLY | 2022-12-31 | Superior |  |  | 120 |  |  | Install a new control building that will be large enough to eventually relocate all the ITCT relaying and controls into it. The new control building will include a dedicated ITCT AC and DC systems large enough to power all ITCTs assets at the substation. All ITCT assets will be cut over to the new dedicated AC/DC system as part of this project. | MI |  |  | Proposed | 2000000 | Engineering | 2021 |  |  |  |  | ITC Transmission | N | N
A in MTEP21 | West | MDU | 19205 | 25417 | LN | 2021-12-31 | Tioga 1 Sub | Str. #54 on TL006-1 |  | 60 |  |  | 60 kV loop line around the city of Tioga | ND |  | 4 | Proposed | 1480722 | Planning | [5 empty] | Montana-Dakota Utilities Company | N | N
A in MTEP21 | West | MDU | 19605 | 25517 | SUB | 2022-06-30 | Beulah |  |  | 115 | 46 |  | Replace Beulah 115/46 kV substation | ND |  |  | Planned | 6000000 | Engineering | [5 empty] | Montana-Dakota Utilities Company | N | N
A in MTEP21 | West | MEC | 2938 | 5113 | LNup | 2022-06-01 | Sub 39 | Cordova | 1 | 345 |  | 1471 | Replace a limited number of existing 345 kV line structures to increase line conductor clearances. This Project will allow higher conductor operating temperatures and result in higher ratings on the Sub 39-MEC Cordova 345 kV line. | IL | 15.45 |  | Planned | 500000 | Planning |  |  | 1471 |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 4247 | 8371 | LNrb | 2022-12-31 | Sub 18 | Sub 85 | 1 | 161 |  |  | Reconductor 3.84 miles of 161 kV line from Sub 85 to Sub 18 | IA,IL | 3.84 |  | Proposed | 1100000 | Planning | 2020 | Estimated rating, may require terminal equipment upgrades to reach 410 MVA |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 4247 | 25875 | TEQ | 2022-12-31 | Sub. 18 |  |  | 161 |  |  | Replace limiting substation terminal equipment at Sub 18 on the Sub 85 161 kV line terminal to uprate the Sub 85-Sub 18 161 kV line | IA |  |  | Proposed | 450000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 4247 | 25872 | TEQ | 2022-12-31 | Sub 85 |  |  | 161 |  |  | Replace limiting substation terminal equipment at Sub 85 on the Sub 18 161 kV line terminal to uprate the Sub 85-Sub 18 161 kV line | IA |  |  | Proposed | 50000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 18885 | 25332 | LNrb | 2020-10-01 | Clarinda | Braddyville | 1 | 161 |  |  | 12.3 mile 161 kV line rebuild from Clarinda to Braddyville substation. Braddyville substation will be constructed to accommodate J611 wind farm request off Clarinda to Maryville 161 kV line. | IA | 12.3 |  | Planned | 6750000 | Budgetary | [5 empty] | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 18890 | 25340 | LNcnv | 2020-12-31 | Clarksville East | Donald Feldman | 1 | 69 |  |  | Convert MidAmerican's Clarksville East-Shell Rock 34.5 kV line to 69 kV. | IA |  |  | Planned | 4488000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 18890 | 25950 | BUS | 2021-12-01 | Clarksville |  |  | 69 |  |  | Project to upgrade the existing 34.5 kV Clarksville East substation to 69 kV. | IA |  |  | Proposed | 901340 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 18891 | 25341 | TEQ | 2020-11-01 | Plymouth |  |  | 161 |  |  | Plymouth 161 kV Switches 9460A, 9440B, 9440L, 9610B, 9610L, 9470B, and 9470L are being replaced due to condition. Also, Switch 9460C is being removed and replaced with bus. When the switches are replaced, the jumpers will also be replaced. | IA |  |  | Planned | 350000 | Budgetary | [5 empty] | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 19745 | 25558 | SUB | 2022-06-01 | 100th & 54th avenue |  |  | 161 |  |  | Replace the 161 kV breaker # 803 that has interrupting rating of 40kA | IA |  |  | Proposed | 250000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 19994 | 25668 | LN | 2022-12-01 | Hospers | Marcus East | 1 | 69 |  |  | Construct a new 69 kV line between Marcus East and Hospers Substations | IA |  |  | Proposed | 16800000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19994 | 25672 | SUB | 2022-12-01 | Marcus East |  |  | 69 |  |  | Rebuild Marcus East Substation to install 69 kV line breakers and a 69 kV capacitor banks. The substation will have three 69 kV line terminals. | IA |  |  | Proposed | 7400000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19994 | 25669 | TEQ | 2022-12-01 | Hospers |  |  | 69 |  |  | Expand Hospers Substation to install new 69 kV line terminal at Hospers Substation for new Hospers-Marcus East 69 kV line. | IA |  |  | Proposed | 1200000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 19997 | 25673 | CB | 2021-12-31 | Sub. Fort Dodge M |  |  | 161 |  |  | Add 161 kV circuit breaker at Sub Fort Dodge M to increase reliability and operational flexibility. | IA |  |  | Proposed | 150000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19997 | 26591 | CB | 2023-12-31 | Avoca |  |  | 161 |  |  | Replace 161 kV breaker at Avoca | IA |  |  | Planned | 450000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19997 | 26214 | SUB | 2022-12-31 | Crescent Bridge |  |  | 69 |  |  | Add new breakers | IL |  |  | Planned | 4100000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19997 | 26209 | CB | 2023-12-31 | CBEC |  |  | 161 |  |  | Replace 161 kV breakers 807, 810, 811, and 812 | IA |  |  | Planned | 800000 | GIA | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19997 | 26208 | SUB | 2022-12-31 | Clarksville East |  |  | 161 |  |  | Substation upgrade. | IA |  |  | Planned | 900000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19997 | 26207 | SUB | 2024-12-31 | Sac City |  |  | 69 |  |  | Add 69 kV breakers. | IA |  |  | Planned | 6500000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19997 | 26206 | CB | 2022-12-31 | Sac City |  |  | 69 |  |  | Sac City 69 kV breaker replacements. | IA |  |  | Proposed | 525000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19997 | 25896 | CB | 2021-12-31 | Lehigh |  |  | 345 |  |  | Replace Lehigh 345 kV breaker to increase reliability and operational flexibility. | IA |  |  | Proposed | 300000 | Budgetary | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19997 | 25895 | CB | 2021-12-31 | Sub Fort Dodge M |  |  | 161 |  |  | 161 kV breaker replacements to increase reliability and operational flexibility. | IA |  |  | Proposed | 4000000 | Budgetary | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 19998 | 25674 | SUB | 2022-12-01 | NW 2nd Street |  |  | 69 |  |  | New 69 kV distribution substation | IA |  |  | Proposed | 7500000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 19998 | 25675 | TAP | 2022-12-01 | NW 2nd Street |  |  | 69 |  |  | New 69 kV Line Work | IA |  |  | Proposed | 2500000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 19999 | 25676 | TX | 2023-06-01 | Booneville |  |  | 345 | 161 |  | Add 2nd 345-161 kV xfmr | IA |  |  | Proposed | 16700000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20000 | 25677 | TX | 2024-12-01 | Bondurant |  |  | 345 | 161 |  | Add 345-161 kV Transformer | IA |  |  | Proposed | 11900000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20002 | 25679 | CAP | 2023-12-01 | Waukee |  |  | 69 |  |  | Install 69 kV capacitor bank and 69 kV breakers | IA |  |  | Proposed | 1600000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20003 | 25682 | SUB | 2024-12-01 | Highway 6 |  |  | 161 | 13.2 |  | New 161/13.2 kV substation | IA |  |  | Proposed | 3100000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20003 | 25683 | TAP | 2024-12-01 | Highway 6 |  |  | 161 |  |  | 161 kV Line Work | IA |  |  | Proposed | 2900000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20006 | 25684 | BUS | 2022-06-01 | DPS |  |  | 161 |  |  | DPS Strain Bus Uprate | IA |  |  | Proposed | 300000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20007 | 25685 | BUS | 2022-03-01 | Clarion |  |  | 69 |  |  | Substation bus expansion | IA |  |  | Proposed | 375000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20008 | 25686 | LNup | 2021-06-01 | Hampton West | Latimer |  | 69 |  |  | Replace structures to obtain maximum conductor rating | IA |  |  | Proposed | 925000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20010 | 25687 | TAP | 2021-12-31 | Sub. 73 |  |  | 69 |  |  | 69 kV line tap work to support converting Sub 73 from a tapped substation to an in-and-out substation with 69 kV line circuit breakers. | IA |  |  | Proposed | 500000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20011 | 25688 | TAP | 2023-06-01 | Sub. 84 |  |  | 69 |  |  | 69 kV line tap work to support converting Sub 84 from a tapped substation to an in-and-out substation with 69 kV line circuit breakers. | IA |  |  | Proposed | 500000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20011 | 25690 | LNup | 2023-06-01 | SUb. 84 | Sub. 85 |  | 69 |  |  | Install OPGW from Sub 84 to Sub 55 for communications and replace structures and conductor on sections of line subject to galloping. | IA |  |  | Proposed | 1400000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20011 | 25689 | LNup | 2023-06-01 | Valley Drive | Sub. 84 |  | 69 |  |  | Install OPGW from Valley Drive to Sub 84 for communications and replace structures and conductor on sections of line subject to galloping. | IA |  |  | Proposed | 3500000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20012 | 25691 | CB | 2023-06-01 | Sub. 17 |  |  | 161 |  |  | Add 161 kV line circuit breaker at Sub 17 on the Sub 28 line terminal to support the addition of a new 161-13.2 kV transformer. | IA |  |  | Proposed | 1000000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20013 | 25692 | SUB | 2022-12-31 | Sub. 113 |  |  | 161 | 69 |  | Add a new 161-69 kV substation bisecting the Oak Grove-Mercer 161 kV line and Sub 108-Sub 111 69 kV line. | IL |  |  | Proposed | 3500000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20013 | 25693 | TAP | 2022-12-31 | Sub. 113 |  |  | 161 |  |  | 161 kV line taps for Sub 113 bisecting the Oak Grove-Mercer 161 kV line | IL |  |  | Proposed | 1500000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20038 | 25735 | TEQ | 2022-12-31 | Sub. 56 |  |  | 161 |  |  | Replace limiting substation terminal equipment at Sub 56 on the Sub 85 161 kV line terminal to uprate the Sub 56-Sub 85 161 kV line | IA |  |  | Proposed | 900000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20121 | 25826 | CAP | 2022-12-31 | Hills |  |  | 345 |  |  | Expand the Hills 345 kV substation yard from a ring bus to a breaker-and-a-half configuration. Add two 150 MVAR, 345 kV capacitor banks. | IA |  |  | Proposed | 12000000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20123 | 25828 | CB | 2021-12-31 | Grimes |  |  | 345 |  |  | Add a new 345 kV breaker to the Grimes 345 kV ring bus to eliminate a NERC TPL-001 Category P2 breaker failure contingency | IA |  |  | Proposed | 1300000 |  | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20125 | 25830 | LNup | 2020-12-31 | Deep River | Parnell | 1 | 161 |  |  | Replace structures to uprate the rating of the J438 POI Deep River-Parnell 161 kV line | IA |  |  | Proposed | 225000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20126 | 25831 | LNrb | 2020-10-01 | Braddyville | Maryville | 1 | 161 |  |  | Reconductor the 161 kV line between the J611 POI Braddyville substation and the Iowa Missouri border. | IA |  |  | Proposed | 500000 | Planning | [5 empty] | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20127 | 25832 | LNup | 2020-08-05 | Macksburg | Winterset | 1 | 161 |  |  | Replace structures to uprate the rating of the Macksburg-Winterset 161 kV line. | IA |  |  | Proposed | 120000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20128 | 25833 | LNup | 2020-06-01 | Montezuma | Diamond Trail | 1 | 345 |  |  | Replace structures to uprate the rating of the Montezuma-J530 POI Diamond Trail 345 kV line | IA |  |  | Proposed | 250000 |  | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20129 | 25834 | LNrb | 2021-12-31 | Diamond Trail | Hills | 1 | 345 |  |  | Reconductor the J530 POI Diamond Trail-Hills 345 kV Line | IA |  |  | Proposed | 27400000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20129 | 25835 | TEQ | 2021-12-31 | Hills |  |  | 345 |  |  | Uprate Hills terminal equipment on Diamond Trail 345 kV line terminal | IA |  |  | Proposed | 400000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20130 | 25836 | LNup | 2021-12-31 | Bondurant | Montezuma | 1 | 345 |  |  | Replace structures to uprate the rating of the Bondurant-Montezuma 345 kV Line | IA |  |  | Proposed | 620000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20153 | 25861 | LNrb | 2022-12-31 | Denver | Waverly | 1 | 69 |  |  | Rebuild 69 kV Denver to Waverly Junction line due to condition and to improve reliability. | IA |  |  | Proposed | 7200000 | Budgetary | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20153 | 26203 | LNrb | 2022-12-31 | Humboldt East | Eagle Grove | 1 | 69 |  |  | Humboldt East - Dakota City - Thor - Eagle Grove 69 kV line | IA |  |  | Planned | 9200000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20153 | 26202 | LNrb | 2021-12-31 | Macedonia | Hastings | 1 | 69 |  |  | Rebuild Macedonia to Hastings 69 kV line. | IA |  |  | Planned | 4000000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20153 | 26199 | LNrb | 2024-12-31 | Sub A | Sub E |  | 69 |  |  | Sub A to Sub E double circuit 69 kV reconductor due to age and to increase reliability | IA |  |  | Planned | 1200000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20153 | 25863 | LNrb | 2022-12-31 | Monroe | Pella |  | 69 |  |  | Rebuild 69 kV Monroe - Otley - W. Pella REC 69 kV line | IA |  |  | Proposed | 5600000 | Budgetary | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20153 | 25862 | LNrb | 2023-12-31 | Sub G | GRS Tap | 1 | 69 |  |  | Rebuild 69 kV lines due to condition an to improve reliability. | IA |  |  | Proposed | 500000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20154 | 25864 | TAP | 2024-12-31 | Humboldt East/Humboldt Central |  |  | 69 |  |  | Install 69 kV line taps into new or existing substations to serve customer load or to improve system reliability. | IA |  |  | Proposed | 1000000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20154 | 26215 | TAP | 2022-12-31 | Crescent Bridge |  |  | 69 |  |  | Add 69 kV line taps | IL |  |  | Planned | 1800000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20154 | 26205 | TAP | 2024-12-31 | Charles City North |  |  | 69 |  |  | Install 69 kV line taps into new or existing substations to serve customer load or to improve system reliability. | IA |  |  | Proposed | 600000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20154 | 26204 | TAP | 2021-12-31 | Dakota City |  |  | 69 |  |  | Dakota City line work | IA |  |  | Planned | 400000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20154 | 25866 | TAP | 2024-12-31 | Sac City Switching station |  |  | 69 |  |  | Install 69 kV line taps into new or existing substations to serve customer load or to improve system reliability. | IA |  |  | Proposed | 600000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20154 | 25865 | TAP | 2022-12-31 | Sub Fort Dodge M |  |  | 69 |  |  | Install 69 kV line taps into new or existing substations to serve customer load or to improve system reliability. | IA |  |  | Proposed | 750000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20155 | 25867 | TEQ | 2024-12-31 | Sycamore |  |  | 345 | 161 |  | Replace existing relaying, communication equipment and control house equipment at several existing substations to increase system reliability and operating flexibility. | IA |  |  | Proposed | 15300000 | Budgetary | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20155 | 26211 | RLY | 2022-12-31 | DPS |  |  | 161 |  |  | Relay replacement at DPS substation | IA |  |  | Planned | 1479000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20155 | 26210 | RLY | 2024-12-31 | Various |  |  | 345 | 161 |  | Substation relay and communication upgrades at various locations | IA,IL |  |  | Planned | 14000000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20155 | 26198 | RLY | 2022-12-31 | Sub. E East Moline |  |  | 161 |  |  | Control building | IL |  |  | Planned | 5900000 | Budgetary | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20155 | 26197 | RLY | 2021-12-31 | Council Bluffs | Glenwood | 1 | 69 |  |  | 69 kV line relay replacement | IA |  |  | Planned | 570000 | Budgetary | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20155 | 25869 | RLY | 2024-12-31 | Council Bluffs |  |  | 345 | 161 |  | Replace 9T1 differential relaying | IA |  |  | Planned | 350000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20155 | 25868 | SUBmisc | 2022-12-31 | Raun |  |  | 345 | 161 |  | New control cable entrance and cable trench replacement. | IA |  |  | Planned | 1400000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20171 | 25929 | LNup | 2022-04-01 | Red Oak | Emerson | 1 | 69 |  |  | Replace structure to obtain the maximum conductor rating of 212 ¿ | IA |  |  | Proposed | 200000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20172 | 25930 | LNup | 2021-12-31 | Percival | Hamburg | 1 | 69 |  |  | Replace structure to obtain the maximum conductor rating of 212 ¿ | IA |  |  | Proposed | 60000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20173 | 25931 | LN | 2023-06-01 | Quick | Sub. 701 | 1 | 161 |  |  | Construct t a new Quick-Sub 701 161 kV line | IA |  |  | Proposed | 14300000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20173 | 25939 | TEQ | 2023-06-01 | Sub 701 |  |  | 161 |  |  | New 161 kV Line Terminal at Sub 701 | IA |  |  | Proposed | 1000000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20173 | 25934 | TEQ | 2023-06-01 | Quick |  |  | 161 |  |  | New 161 kV Line Terminal at Quick Substation | IA |  |  | Proposed | 1700000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20175 | 25935 | SwSta | 2021-09-15 | Remsen Township |  |  | 345 |  |  | The 345 kV Interconnection Substation will consist of a 345 kV ring bus, three 345 kV breakers, two 345 kV dead-end structures, and associated equipment. | IA |  |  | Proposed | 11700000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20175 | 25936 | TAP | 2021-09-15 | Remsen Township |  |  | 345 |  |  | Line Taps for Remsen Township Substation | IA |  |  | Proposed | 1500000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20176 | 25937 | TAP | 2022-06-01 | Hitchcock |  |  | 69 |  |  | New 69 kV line taps into distribution substation | IA |  |  | Proposed | 3600000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20177 | 25938 | TAP | 2023-06-01 | Missouri Valley East |  |  | 69 |  |  | New 69 kV line taps into distribution substation | IA |  |  | Proposed | 800000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20178 | 25944 | TEQ | 2021-12-01 | Webster |  |  | 161 |  |  | Expansion of Webster 161 kV to accommodate J524 | IA |  |  | Proposed | 3050000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20189 | 25952 | RLY | 2021-06-01 | Washburn |  |  | 161 |  |  | Washburn Bus A: Same upgrades needed on Bus A as are being completed on Bus B under T91PK. The 161 kV circuit switcher on 161-69 kV transformer does not interrupt faults | IA |  |  | Proposed | 1002400 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20192 | 25954 | CB | 2021-12-31 | Rock Valley |  |  | 69 |  |  | Replace two 69 kV oil circuit breakers and electromechanical line and bus relaying at Rock Valley Substation | IA |  |  | Proposed | 1100000 |  | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20626 | 26057 | SUB | 2022-02-04 | Se Soteria |  |  | 161 | 13.2 |  | Add new transformer | IA |  |  | Proposed | 10000000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20626 | 26058 | TAP | 2022-02-04 | Se Sotoria |  |  | 161 |  |  | Add line taps | IA |  |  | Proposed | 15300000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 20627 | 26059 | SUB | 2022-01-01 | Johnson Creek |  |  | 161 | 13.2 |  | Add new transformer and breakers | IA |  |  | Proposed | 10000000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 20627 | 26060 | TAP | 2022-01-01 | Johnson Creek |  |  | 161 |  |  | Add 161 kV taps | IA |  |  | Proposed | 15300000 | Planning | 2020 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 21265 | 26212 | SUB | 2022-12-31 | Sub. A |  |  | 161 | 69 |  | Replace 69 kV breakers and protective relaying. Also replace 161-69 kV transformer bank 8T1 and 8T2 with a new 161-69 kV 125 MVA transformer. | IA |  |  | Planned | 4100000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 21266 | 26213 | TX | 2021-08-31 | Plymouth |  |  | 161 | 69 |  | Replace 161/69 kV transformer | IA |  |  | Planned | 1100000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 21266 | 26321 | TX | 2022-09-30 | Plymouth |  |  | 161 | 69 |  | Purchase new 161 to 69 kV transformer to replenish the spare used. | IA |  |  | Planned | 2300000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 |  | MEC | 21266 | 26320 | IND | 2021-12-31 | Plymouth |  |  | 13 |  |  | Retire 13 kV reactors | IA |  |  | Planned | 200000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 21430 | 26266 | TX | 2022-09-30 | Grimes |  |  | 345 | 161 | 560 MVA | Replace the 345/161 kV 560 MVA transformer at Grimes substation which failed recently. The new replacement transformer will be added as a spare 345/161kV 560 MVA transformer at Grimes substation. | IA |  |  | Planned | 3000000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 21430 | 26268 | TX | 2021-07-31 | Grimes |  |  | 345 | 161 |  | Remove the failed transformer at Grimes and replace it with existing spare. | IA |  |  | Planned | 500000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 21430 | 26267 | IND | 2021-12-31 | Grimes |  |  | 13.8 |  |  | There are two 13.8 kV reactors on the tertiary of the failed transformer. One has a failed RL Switcher and the other 13.8 kV reactor has a failed phase. Given this failed reactor equipment on the tertiary and after reviews by our system control group and planning, we are not replacing the failed reactor equipment when we put the transformer in-service. The equipment will be retired/saved for spares as appropriate, likely later this year. | IA |  |  | Planned | 350000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | West | MEC | 21545 | 26289 | LNup | 2022-09-15 | Diamond Trail | Hills | 1 | 345 |  |  | Replace the line structure of 345 kV line due to age and condition. | IA |  |  | Planned | 3750000 | Planning | 2021 |  |  |  |  | MidAmerican Energy Company | N | N
A in MTEP21 | East | METC | 17965 | 24731 | SUB | 2022-03-31 | Stonehill |  |  | 138 |  |  | Construct a new 138 kV three breaker ring switching station. | MI |  |  | M3_Long Lead Materials | 5560000 | Engineering | 2020 |  |  | Project is tracking on schedule. | Minor scope and cost estimate changes | METC | N | N
A in MTEP21 |  | METC | 17965 | 25301 | RLY | 2022-03-31 | Denso Jackson |  |  | 138 |  |  | Install Relay at tap to support anti-islanding | MI |  |  | M3_Long Lead Materials | 77051 | Engineering | 2020 |  |  | Project is tracking on schedule. | Design costs were higher than originally expected. | METC | N | N
A in MTEP21 |  | METC | 17965 | 25300 | RLY | 2022-03-31 | Vrooman |  |  | 138 |  |  | Relay upgrades for anti-islanding | MI |  |  | M3_Long Lead Materials | 64429 | Engineering | 2020 |  |  | Project is tracking on schedule. | Design costs were higher than originally expected. | METC | N | N
A in MTEP21 | East | METC | 17965 | 24739 | RLY | 2022-03-31 | Rice Creek |  |  | 138 |  |  | Protection and control upgrades at Rice Creek. | MI |  |  | M3_Long Lead Materials | 311471 | Engineering | 2020 |  |  | Project is tracking on schedule. | Design costs were higher than originally expected. | METC | N | N
A in MTEP21 | East | METC | 17965 | 24733 | LINE | 2022-03-31 | Rice Creek | Vrooman |  | 138 |  |  | Cut the Rice Creek - Vrooman 138 kV circuit into the new J806 interconnection switching station and install OPGW for anti-islanding | MI |  |  | M3_Long Lead Materials | 6215460 | Engineering | 2020 |  |  | Project is tracking ahead of schedule. | Scope Changes caused project cost estimate to increase due to additional project requirements from underground fiber. | METC | N | N
A in MTEP21 | East | METC | 18239 | 25065 | SUB | 2023-12-31 | Various |  |  | 345 | 138 |  | Replace aging and outdated equipment at a pace that will insure each type of equipment is replaced near its projected end of life. | MI |  |  | Proposed | 36000000 | Budgetary | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 18404 | 25204 | SUB | 2022-06-01 | Nelson Rd |  |  | 345 |  |  | Install the 22H9 Breaker at Nelson Rd to complete the row | MI |  |  | Proposed | 1530894 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19365 | 25466 | LN | 2022-09-01 | Blackstone | Marshal | 1 | 138 |  |  | Extend the Blackstone - Marshall 138kV line by adding 2.5 miles of 954 ACSR DCt to loop in Stable 138kV station. | MI |  | 5 | M2a_Pre-Project Approval | 12730000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19365 | 25467 | SUB | 2022-09-01 | 138 |  |  | 138 |  |  | Install two 138kV 40 kV breakers at Stable 138kV (J857 Interconnection station). | MI |  |  | M2a_Pre-Project Approval | 2230000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19385 | 25468 | LINE | 2022-12-31 | Stonehill | Vrooman |  | 138 |  |  | Remediate the sag limit on the J806 POI – Denso Jackson 138kV line segment. Rebuild approximately 2 miles of the J806 POI – Vrooman 138kV line segment utilizing 1431 ACSR. | MI | 2 |  | M2a_Pre-Project Approval | 6308000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19425 | 25478 | LNup | 2021-12-31 | Bullock | Saginaw River | 1 | 138 |  |  | Raise the sag limits on the Gleaner Tap - Hackett Tap and Hackett - Laundra Tap line segments of the Bullock - Saginaw River 138kV line. | MI | 6.53 |  | M2a_Pre-Project Approval | 830000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19445 | 25479 | SUB | 2022-09-01 | Stable |  |  | 138 |  |  | Construct Stable 138kV as a ring bus station with three 40kA breakers for the J857 interconneciton. | MI |  |  | M2a_Pre-Project Approval | 5958354 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19445 | 25481 | RLY | 2022-09-01 | Rice Creek |  |  | 138 |  |  | Upgrade Pos 577 Relaying | MI |  |  | M2a_Pre-Project Approval | 506754 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19445 | 25480 | LINE | 2022-09-01 | Mud Lake | Foundry |  | 138 |  |  | Extend the Mud Lake - Foundry 138kV line by adding 0.1 miles of 954ACSR DCt to loop in Stable 138kV. Install OPGW from Stable to Brewer street and to Foundry. | MI |  | 0.1 | M2a_Pre-Project Approval | 4388400 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19465 | 25482 | LNup | 2021-12-31 | Parr Road | J875 Interconnection |  | 138 |  |  | Remediate the sag to no less than 145 MVA. This will require one new structure. | MI |  |  | M2a_Pre-Project Approval | 84000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19465 | 25483 | LNup | 2021-12-31 | Whiting | J875 Interconnection |  | 138 |  |  | Remediate the sag on the J875 Interconnection - Raisin Tap line segment to no less tna 197 MVA. This will require three new structures. | MI |  |  | M2a_Pre-Project Approval | 254400 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19506 | 25492 | RLY | 2022-12-13 | McGulpin |  |  | 138 |  |  | Replace BM5 Relays. Install dual-pilot relay protection on the METC Mcgulpin-Riggsville 138kV circuit. | MI |  |  | M2a_Pre-Project Approval | 473000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19506 | 25494 | RLY | 2022-12-13 | Livingston |  |  | 138 |  |  | Replace WM9 Relays. Install dual-pilot relay protection on the METC Riggsville-Livingston 138kV circuit. | MI |  |  | M2a_Pre-Project Approval | 331000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19506 | 25493 | SUB | 2022-12-13 | Riggsville |  |  | 138 |  |  | Install dual-pilot relay protection on the METC Riggsville-Livingston 138kV circuit as well as the METC Mcgulpin-Riggsville 138kV circuit. Remove bypass switches 207 & 307 and breaker sparing functionality associated with breakers 277 & 377. | MI |  |  | M2a_Pre-Project Approval | 683000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19546 | 25531 | SUB | 2022-11-18 | Tangent |  |  | 138 |  |  | Install a new 138 kV station with 3-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. | MI |  |  | M3_Long Lead Materials | 5540862 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 |  | METC | 19546 | 26248 | SUBmisc | 2022-11-18 | Morocco |  |  | 138 |  |  | Install fiber optic patch cables. Create communication path from Tangent to Whiting. | MI |  |  | M3_Long Lead Materials | 45282 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 |  | METC | 19546 | 26247 | SUBmisc | 2022-11-18 | Beecher |  |  | 138 |  |  | Install fiber optic patch cables. Create communication path from Tangent to Whiting. | MI |  |  | M3_Long Lead Materials | 183854 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 |  | METC | 19546 | 26246 | COM | 2022-11-18 | Tangent | Raisin Tap |  | 138 |  |  | Install overhead fiber from Tangent to Raisin Tap and connect to the OPGW on the Raisin Tap. Install 2nd OPGW bundle from Tangent to approximately Structure #084A4759 to connect underground fiber to Parr Rd. | MI | 2.5 |  | M3_Long Lead Materials | 1890000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 |  | METC | 19546 | 26245 | COM | 2022-11-18 | Leoni | METC Structure 010A314 |  | 138 |  |  | Install overhead fiber from Leoni to Structure #010A314. | MI | 0.25 |  | M3_Long Lead Materials | 430800 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 |  | METC | 19546 | 26244 | COM | 2022-11-18 | Beecher | METC Structure 017E9231 |  | 138 |  |  | Install overhead fiber from Beecher to Structure #017E9231 | MI | 1.7 |  | M3_Long Lead Materials | 669600 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19546 | 26037 | COM | 2022-11-18 | Raisin Tap | Raisin |  | 138 |  |  | Install approximately 7.3 miles of OPGW on the Raisin Tap - Raisin Substation line segment. | MI | 7.3 |  | M3_Long Lead Materials | 2112000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19546 | 25536 | COM | 2022-11-18 | Leoni | Parr Road, Tangent, and Whiting |  | 138 |  |  | Install approximately 12.5 miles of underground fiber optic for the Parr Road - Tangent 138kV circuit. Install approximately 30 miles of underground fiber optic for the Tangent - Whiting 138kV circuit. Install approximately 18.5 miles of underground fiber optic for the Leoni - Parr Road 138kV circuit. | MI | 61 |  | M3_Long Lead Materials | 21135600 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19546 | 25535 | SUBmisc | 2022-11-18 | Leoni |  |  | 138 |  |  | Install required relay upgrades at Leoni to interconnect J875 | MI |  |  | M3_Long Lead Materials | 565877 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19546 | 25534 | SUBmisc | 2022-11-18 | Whiting |  |  | 138 |  |  | Install required relay upgrades at Whiting to interconnect J875 | MI |  |  | M3_Long Lead Materials | 231797 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19546 | 25533 | SUBmisc | 2022-11-18 | Parr Road |  |  | 138 |  |  | Install required relay upgrades at Parr Rd to interconnect J875 | MI |  |  | M3_Long Lead Materials | 563477 | GIA | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19546 | 25532 | LINE | 2022-11-18 | Parr Road | Whiting |  | 138 |  |  | Loop the Parr Road - Whiting 138kV circuit into the new METC 138kV Tangent station. | MI |  |  | M3_Long Lead Materials | 3154800 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19606 | 25518 | SUBmisc | 2021-12-31 | Thetford |  |  | 345 |  |  | Upgrade station equipment at Thetford 345kV positions 33R8, RH33, and 33H9. | MI |  |  | M3_Long Lead Materials | 189000 | Engineering | 2019 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19606 | 25519 | LNup | 2021-12-31 | Thetford | Jewell |  | 345 |  |  | Reconductor approximately 0.05 miles of the Thetford-Jewell 345kV circuit. Replace existing 2156 ACSR with a conductor rated at least that of 2-954 ACSR. Remediate the sag on the Thetford - Jewell 345kV circuit. | MI | 0.05 |  | M3_Long Lead Materials | 660000 | Engineering | 2019 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19625 | 25522 | LNup | 2021-12-31 | Bauer | Pontiac |  | 345 |  |  | Remediate the sag on the Bauer - Pontiac 345kV circuit. Replace four (4) 345kV double circuit structures. | MI |  |  | M3_Long Lead Materials | 1879000 | Engineering | 2019 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19970 | 25653 | LNrb | 2024-12-31 | Alma | Vestaburg | 1 | 138 |  |  | Rebuild approximately 0.43 mile of the Alma - Vestaburg 138kV circuit using 954 ACSR on double circuit structures constructed at 138kV Standards with OPGW. | MI |  |  | Proposed | 2730000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19970 | 25654 | TEQ | 2024-12-31 | Alma |  |  | 138 |  |  | Replace terminal equipment at Alma | MI |  |  | Proposed | 70000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19985 | 25657 | SUB | 2021-11-01 | Murphy |  |  | 138 |  |  | Expand Murphy 138kV by adding Row 12. Install two 63kA breakers. | MI |  |  | M3_Long Lead Materials | 2000250 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 19991 | 25665 | TEQ | 2022-12-31 | Throughout System |  |  | 138 |  |  | Install or replace an existing a new 138 kV, 2-way, full-load-break pole top switch at various tap points across the METC system. | MI |  |  | Proposed | 2000000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20018 | 25701 | LNrb | 2025-06-01 | Bullock | Shale | 1 | 138 |  |  | Rebuild the Bullock to Structure 006A6682 (approximately 5 miles) utilizing 954 ACSR conductor with 230 kV double circuit structure standards with OPGW. Rebuild from Structure 006A6682 to the future Shale Substation (approximately 15 miles) utilizing 954 ACSR conductor with 138 kV double circuit structures standards with OPGW | MI | 20 |  | Proposed | 32960000 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20018 | 25702 | TEQ | 2025-06-01 | Bullock |  |  | 138 |  |  | Upgrade terminal station equipment | MI |  |  | Proposed | 40000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20033 | 25731 | LNup | 2025-06-01 | Weadock | Carter Jct | 1 | 138 |  |  | ITC is to remove the sag limit on the 336 ACSR and raise the sag limit on the 636 ACSR to 158F on the Weadock – Carter Jct 138 kV Line. | MI |  |  | Proposed | 888000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20047 | 25745 | SUBmisc | 2024-12-31 | Blanket for Customer Interconnections | Throughout System |  | 138 |  |  | Blanket for customer interconnections and retirements less than $1 million with in service dates in the year 2024. | MI |  |  | Proposed | 2000000 | Budgetary | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20049 | 25748 | LNup | 2025-06-01 | Gallagher | Twining | 1 | 138 |  |  | The proposed solution is to Raise the sag limit on the 336 ACSR between Gallagher and Withey Lake Jct. and replace the 1/0 Copper on the Withey Lake Jct. - Twinning 138kV line with 477 ACSR utilizing standard 138 kV double circuit structures | MI |  |  | Proposed | 971000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20053 | 25755 | TEQ | 2023-12-31 | Warren |  |  | 138 |  |  | Upgrade Warren 188 terminal equipment to meet or exceed the rating of a 954 ACSR conductor. | MI |  |  | Proposed | 159000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20054 | 25756 | TEQ | 2023-12-31 | Warren |  |  | 138 |  |  | Upgrade terminal station equipment, including a 138 kV breaker, at Warren position 377 to meet or exceed the rating of a 954 ACSR conductor. | MI |  |  | Proposed | 1050000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20108 | 25809 | LN | 2024-12-31 | Atlanta |  |  | 138 |  |  | Split Atlanta-Karn-Thetford into two line | MI |  |  | Proposed | 322000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20118 | 25824 | SUB | 2023-04-01 | Higgins |  |  | 138 |  |  | Expand the 138 kV ring bus by installing 1 additional 138 kV breaker and associated disconnects | MI |  |  | Proposed | 3999698 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 |  | METC | 20118 | 26280 | LN | 2023-04-01 | Higgins | MioDam |  | 138 |  |  | Reterminate the Higgins - Mio Dam 138kV line at Section 50 at Higgins. | MI |  |  | Proposed | 279600 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 |  | METC | 20118 | 26101 | LN | 2023-04-01 | Higgins | Beaver Creek |  | 138 |  |  | Reterminate the Beaver Creek - Higgins 138kV line at Section 10 at Higgins. | MI |  |  | Proposed | 211200 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20120 | 25825 | TEQ | 2023-12-31 | Wackerly |  |  | 138 |  |  | Replace station equipment in the Wackerly Substation meet or exceed rating of a 795 ACSR conductor | MI |  |  | Proposed | 142000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20144 | 25848 | TX | 2025-12-31 | Argenta |  |  | 345 | 138 |  | Replace the Argenta #2 345/138kV transformer. | MI |  |  | Proposed | 5400000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20145 | 25849 | TX | 2025-12-31 | Tallmadge |  |  | 345 | 138 |  | Replace the Tallmadge #2 345/138kV transformer. | MI |  |  | Proposed | 6100000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20146 | 25850 | TX | 2023-12-31 | Tittabawassee |  |  | 345 | 138 |  | Replace the Tittabawassee #1 345/138kV transformer. | MI |  |  | Proposed | 6200000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20147 | 25851 | TX | 2023-12-31 | Vergennes |  |  | 345 | 138 |  | Replace the Vergennes #2 345/138kV transformer. | MI |  |  | Proposed | 7100000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20158 | 25874 | SwSta | 2025-06-01 | New Station (Clinton Jct Replacement) |  |  | 138 |  |  | Replace the Clinton Jct. Tap by configuring a new 3 breaker ring bus 138 kV station and cutting it in the Delhi – Island Rd 138 kV line utilizing 954 ACSR on standard 138 kV double circuit structures with OPGW | MI |  |  | Proposed | 5900000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20158 | 25879 | RLY | 2025-06-01 | Oneida |  |  | 138 |  |  | Install fiber terminations | MI |  |  | Proposed | 9000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20158 | 25878 | RLY | 2025-06-01 | Island |  |  | 138 |  |  | Replace Relaying | MI |  |  | Proposed | 370000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20158 | 25877 | RLY | 2025-06-01 | Delhi |  |  | 138 |  |  | Replace Relaying | MI |  |  | Proposed | 386000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20158 | 25876 | LN | 2025-06-01 | New Station (Clinton Jct Replacement) | Delhi/Island Rd | 1 | 138 |  |  | Cut in Delhi – Island Rd 138 kV line utilizing 954 ACSR on standard 138 kV double circuit structures with OPGW | MI |  |  | Proposed | 4100000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20162 | 25885 | SwSta | 2025-12-31 | Claremont |  |  | 138 |  |  | rebuild Claremont 138 kV station with a new control house at a new site just to the southwest of the existing site utilizing new equipment in a five-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called New Station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI |  |  | Proposed | 17500000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 |  | METC | 20162 | 26230 | SUBmisc | 2025-12-31 | Claremont |  |  | 138 |  |  | Remove transmission equipment at Claremont | MI |  |  | Proposed | 2300000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20162 | 25894 | LN | 2025-12-31 | Claremont (CE TB#3) | New Station | TB3 | 138 |  |  | Redirect Claremont TB3 from Claremont into the new station | MI |  |  | Proposed | 475000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20162 | 25893 | LN | 2025-12-31 | Claremont (CE TB#1) | New Station | TB1 | 138 |  |  | Redirect Claremont TB1 from Claremont into the new station | MI |  |  | Proposed | 495000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20162 | 25892 | LN | 2025-12-31 | Lawndale | Claremont |  | 138 |  |  | Redirect Lawndale - Claremont 138 kV line from Claremont into the new station | MI |  |  | Proposed | 448000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20162 | 25891 | LN | 2025-12-31 | Cornell #2 | Claremont | 2 | 138 |  |  | Redirect Cornell #2 - Claremont 138 kV line from Claremont into the new station | MI |  |  | Proposed | 444000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20162 | 25890 | LN | 2025-12-31 | Cornell #1 | Claremont | 1 | 138 |  |  | Redirect Cornell #1 - Claremont 138 kV line from Claremont into the new station | MI |  |  | Proposed | 440000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20162 | 25889 | LN | 2025-12-31 | Manning #2 | Claremont | 2 | 138 |  |  | Redirect Manning #2 - Claremont 138 kV line from Claremont into the new station | MI |  |  | Proposed | 535000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20162 | 25888 | LN | 2025-12-31 | Manning #1 | Claremont | 1 | 138 |  |  | Redirect Manning #1 - Claremont 138 kV line from Claremont into the new station | MI |  |  | Proposed | 530000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20162 | 25887 | LN | 2025-12-31 | Holland Road | Claremont | 1 | 138 |  |  | Redirect Holland Road - Claremont 138 kV line from Claremont into the new station | MI |  |  | Proposed | 530000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20162 | 25886 | LN | 2025-12-31 | Grey Iron | Claremont |  | 138 |  |  | Redirect Grey Iron - Claremont 138 kV line from Claremont into the new station | MI |  |  | Proposed | 530000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20164 | 25905 | SwSta | 2023-12-31 | Wealthy Street |  |  | 138 |  |  | Rebuild Wealthy Street 138 kV station with a new control house at a new site just to the southwest of the existing site utilizing new equipment in a four-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called New Station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI |  |  | Proposed | 17000000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 |  | METC | 20164 | 26216 | SUBmisc | 2023-12-31 | Wealthy |  |  | 138 |  |  | Remove equipment at Wealthy | MI |  |  | Proposed | 2000000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20164 | 25911 | LN | 2023-12-31 | Wealthy Street CE TB#7 | New Station | TB7 | 138 |  |  | Wealthy Street TB7 from Wealthy Street into the new station | MI |  |  | Proposed | 830000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20164 | 25910 | LN | 2023-12-31 | Wealthy Street CE TB#6 | New Station | TB6 | 138 |  |  | Wealthy Street TB6 from Wealthy Street into the new station | MI |  |  | Proposed | 830000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20164 | 25909 | LN | 2023-12-31 | Northridge | New Station | 1 | 138 |  |  | Redirect Four Mile (Northridge) - Wealthy Street #1 138 kV line from Wealthy Street into the new station | MI |  |  | Proposed | 1250000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20164 | 25908 | LN | 2023-12-31 | Tallmadge | New Station | 2 | 138 |  |  | Redirect Tallmadge - Wealthy Street #2 138 kV line from Wealthy Street into the new station | MI |  |  | Proposed | 495000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20164 | 25907 | LN | 2023-12-31 | Tallmadge | New Station | 1 | 138 |  |  | Redirect Tallmadge - Wealthy Street #1 138 kV line from Wealthy Street into the new station | MI |  |  | Proposed | 495000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20164 | 25906 | LN | 2023-12-31 | Beals Road | New Station | 1 | 138 |  |  | Redirect Beals Road - Wealthy Street 138 kV line from Wealthy Street into the new station | MI |  |  | Proposed | 1100000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20711 | 26071 | SUBmisc | 2021-06-01 | Stamping Plant |  |  | 138 |  |  | Decommission Stamping Plant Station and remove all equipment. | MI |  |  | M5_In Service | 848000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20711 | 26073 | LINE | 2021-06-01 | Stamping Plant | Beals Road | 1 | 138 |  |  | Terminate 138kV lines and bypass Stamping Plant 138kV station at structure #068C134. Tie Gaines – Stamping Plant to Stamping Plant – Beals Road to create Gaines – Beals Road 138kV line. | MI |  |  | M5_In Service | 203000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20711 | 26072 | LINE | 2021-06-01 | Stamping Plant | Gaines | 1 | 138 |  |  | Terminate 138kV lines and bypass Stamping Plant 138kV station at structure #068C134. Tie Gaines – Stamping Plant to Stamping Plant – Beals Road to create Gaines – Beals Road 138kV line. | MI |  |  | M5_In Service | 203000 | Engineering | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 20826 | 26103 | SUBmisc | 2023-01-01 | Twining |  |  | 138 |  |  | Deadend and equipment necessary to facilitate termination of new 138kV line as well as installation of SSVTs. | MI |  |  | Proposed | 571795 |  | 2022 |  |  |  |  | METC | N | N
A in MTEP21 |  | METC | 20826 | 26290 | RLY | 2023-01-01 | Twining | Arenac | 1 | 138 |  |  | Install underground fiber between Twining and the new CE Arenac station. | MI |  | 0.4 | Proposed | 302736 |  | 2022 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 20826 | 26104 | LN | 2023-01-01 | Twining | Arenac | 1 | 138 |  |  | Installation of new 138kV line and fiber. | MI |  | 0.4 | Proposed | 1220400 |  | 2022 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 21025 | 26126 | LN | 2022-09-01 | Stable | Rice Creek |  | 138 |  |  | Create the Stable (J857 Interconnection Station) - Rice Creek 138kV line by disconnecting the Foundry Spur at structure 074B28. | MI |  |  | M2a_Pre-Project Approval | 398400 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 21025 | 26128 | SUBmisc | 2022-09-01 | Foundry |  |  | 138 |  |  | Decommission all assets at Foundry 138kV | MI |  |  | M2a_Pre-Project Approval | 689222 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 21025 | 26127 | LNup | 2022-09-01 | Stable | Rice Crek |  | 138 |  |  | Install a switch near structure 074B28 for Calhoun tap. | MI |  |  | M2a_Pre-Project Approval | 614400 | Engineering | 2020 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 21046 | 26134 | IND | 2023-12-31 | Livingston |  |  | 345 |  |  | Replace Livingston 345kV shunt reactor 34F | MI |  |  | Proposed | 2500000 | Planning Preliminary | [5 empty] | METC | N | N
A in MTEP21 | East | METC | 21208 | 26195 | LINE | 2025-06-01 | Island Rd | Delhi | 1 | 138 |  |  | Cut into the Island Rd – Delhi 138 kV line at the Clinton Junction with a new double tap structure and install pole top switches at the Packard and Eaton Rapids taps. | MI |  |  | Proposed | 3300000 | Engineering | 2021 |  |  |  |  | METC | N | N
A in MTEP21 | East | METC | 21305 | 26231 | RLY | 2023-06-01 | North Belding |  |  | 138 |  |  | Install new Control House at North Belding 138kV station. Migrate relaying and vacate old control houses. Install SSVTs and Battery system. | MI |  |  | Proposed | 1960830 | [6 empty] | METC | N | N
A in MTEP21 | West | MP | 18066 | 24901 | CB | 2023-12-31 | Badoura |  |  | 115 |  |  | Replace existing circuit breaker & associated equipment | MN |  |  | Proposed | 0 | Planning | 2019 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 |  | MP | 18066 | 26108 | LNrl | 2023-12-31 | Badoura | Hubbard |  | 115 |  |  | Relocate existing 48 Line into ring bus in new yard (deadend outside yard). NOTE: winter ratings increased. | MN | 0 | 0.1 | Proposed | 490000 | Planning | 2021 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 |  | MP | 18066 | 26107 | LNrl | 2023-12-31 | Badoura | Dog Lake |  | 115 |  |  | Relocate 40 Line to ring bus in new substation (deadend outside substation) | MN | 0 | 0.1 | Proposed | 580000 | Planning | 2021 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 | West | MP | 18066 | 24903 | CB | 2023-12-31 | Badoura |  |  | 115 |  |  | Add two breakers in existing ring bus to accommodate relocated lines. Also includes new relay panels. | MN |  |  | Proposed | 750000 | Planning | 2021 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 | West | MP | 18945 | 25719 | LNup | 2021-03-31 | Iron Range | 98L Tap |  | 230 |  | 470/551 | Approximately 21 structure replacements on existing Iron Range-98L Tap 230 kV Line, no ratings impact. | MN | 63.83 |  | Planned | 2130000 | Engineering Preliminary | 2020 |  | 518/606 |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 | West | MP | 20032 | 25743 | SUB | 2023-06-01 | Canosia Road |  |  | 115 | 34.5 |  | Add two 115 kV circuit breakers and bus work to complete 4 position ring bus (3 positions with 2 breakers are existing). High-side terminal equipment to accommodate a new 115/34.5 kV transformer. | MN |  |  | Proposed | 1500000 | Planning Preliminary | 2020 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 | West | MP | 20075 | 25776 | CAP | 2025-12-31 | Forbes 230 |  |  | 230 |  |  | Replace aging 230 kV capacitor bank | MN |  |  | Proposed | 1100000 | Engineering Preliminary | 2021 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 |  | MP | 20075 | 26228 | TX | 2025-12-31 | Forbes 230 |  |  | 230 |  |  | Replace Forbes 3TR 230/115 kV 373 MVA Transformer and foundation | MN |  |  | Proposed | 3050000 | Engineering Preliminary | 2021 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 |  | MP | 20075 | 26227 | TEQ | 2025-12-31 | Forbes 230 |  |  | 230 |  |  | Replace or upgrade 230 kV disconnect switches, wave traps, ccvt's, and control panels; improve substation grounding | MN |  |  | Proposed | 1800000 | Engineering Preliminary | 2021 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 | West | MP | 20075 | 25777 | CB | 2025-12-31 | Forbes 230 |  |  | 230 |  |  | Replace a 230 kV oil circuit breaker and a older 230 kV SF6 oil circuit breaker at Forbes | MN |  |  | Proposed | 1400000 | Engineering Preliminary | 2021 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 | West | MP | 20081 | 25790 | CAP | 2022-12-31 | Stinson 115 |  |  | 115 |  |  | Replace existing problematic capacitor bank with a 28 MVAR bank. | WI |  |  | Proposed | 970000 | Engineering | 2020 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 | West | MP | 20081 | 25792 | CB | 2022-12-31 | Stinson 115 |  |  | 115 |  |  | Replace 115W Breaker | WI |  |  | Proposed | 200000 | Engineering | 2020 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 | West | MP | 20081 | 25791 | TEQ | 2022-12-31 | Stinson 115 |  |  | 115 |  |  | Replace switches, panels, arresters, PT's, and jumper. | WI |  |  | Proposed | 360000 | Engineering | 2020 |  |  |  |  | Minnesota Power (Allete, Inc.) | N | N
A in MTEP21 |  | MP | 20143 | 25925 | RLY | 2022-08-26 | Wing River |  |  | 230 |  |  | MP metering equipment upgrades | MN |  |  | Proposed | 475000 | Engineering | 2020 |  |  |  |  | Great River Energy | N | N
A in MTEP21 | West | MPC | 19325 | 25461 | LNrb |  | Hensel 69 kV | Glasston 69kV | 1 | 69 |  |  | Rebuild to 115 kV (operated at 69 kV) with 477 ACSR | ND |  |  | Planned | [7 empty] | Minnkota Power Cooperative | N | N
A in MTEP21 | West | MPC | 19325 | 25463 | LNrc |  | Lincoln 69 kV | Bowesmont 69 kV | 1 | 69 |  |  | Reconductor with 477 ACSR | ND |  |  | Planned | [7 empty] | Minnkota Power Cooperative | N | N
A in MTEP21 | West | MPC | 19325 | 25462 | LNrb |  | Glasston 69 kV | Lincoln 69 kV | 1 | 69 |  |  | Rebuild to 115 kV (operated at 69 kV) with 477 ACSR | ND |  |  | Planned | [7 empty] | Minnkota Power Cooperative | N | N
A in MTEP21 | West | MPC | 19765 | 25561 | Dist | 2020-11-01 | Berg |  |  | 69 |  |  | New substation on Prairie-Coleman 69 kV line | ND |  |  | Planned | 3600000 | Budgetary | [5 empty] | Minnkota Power Cooperative | N | N
A in MTEP21 | West | MPC | 19766 | 25562 | GEN | 2023-09-15 | MPC03000 Int Sub |  |  | 69 |  |  | Interconnection substation and generator on Redby-Quiring Jct 69 kV | MN |  |  | Planned | 670000 | Budgetary | [5 empty] | Minnkota Power Cooperative | N | N
A in MTEP21 | West | MRES | 17996 | 24768 | TX | 2022-05-01 | Willmar |  |  | 230 | 115 |  | Add a 230/115 kV transformer at Willmar | MN |  |  | Proposed | 5344403 | Planning | 2020 |  |  |  |  | Great River Energy | N | N
A in MTEP21 |  | MRES | 17996 | 26109 | LNup | 2022-05-01 | Priam | Willmar | 1 | 115 |  |  | Line and substation modifications to accommodate the Priam - Willmar 115 kV line. | MN |  |  | Proposed | 1200000 | Planning | 2021 |  |  |  |  | Great River Energy | N | N
A in MTEP21 | West | MRES | 19845 | 25573 | CB | 2021-12-31 | South |  |  | 69 |  |  | Replace oil filled breakers due to age and condition. | MN |  |  | M4_Pre-Construction | 800000 | Budgetary | [5 empty] | Missouri River Energy Services (MRET) | N | N
A in MTEP21 | West | MRES | 19846 | 25574 | SUB | 2021-12-31 | Plant |  |  | 69 |  |  | Relocate substation due to power plant decommissioning. | MN |  |  | M4_Pre-Construction | 3000000 | Budgetary | [5 empty] | Missouri River Energy Services (MRET) | N | N
A in MTEP21 | West | MRES | 19846 | 25575 | Dist | 2021-12-31 | Plant Substation |  |  | 69 |  |  | Relocating distribution equipment associated with the Plant Substation. | MN |  |  | Planned | 0 | Budgetary |  | Distribution costs of $1,500,000. Facility cost set to $0 as distribution cost should not be counted in MTEP. |  |  |  | Missouri River Energy Services (MRET) | N | N
A in MTEP21 | West | MRES | 19986 | 25655 | CB | 2022-12-30 | Willmar |  |  | 230 | 69 |  | Replace Oil filled breaker due to age and condition. | MN |  |  | Planned | 500000 | Budgetary | [5 empty] | Missouri River Energy Services (MRET) | N | N
A in MTEP21 |  | MRES | 19986 | 25656 | TEQ | 2022-12-30 | Willmar |  |  | 230 | 69 |  | Replace jumpers and switches due to age and condition. | MN |  |  | Planned | 110000 | Budgetary | [5 empty] | Missouri River Energy Services (MRET) | N | N
A in MTEP21 |  | MRES | 20148 | 25854 | LN | 2026-07-31 | Benson | Benson Muni | 1 | 115 |  |  | Build 2 miles of new 115 kV transmission line from end of GRE ownership of Appleton to Benson to Benson Muni and two new 115 kV breakers. | MN |  | 2 | Proposed | 3000000 | Planning | 2020 |  |  |  |  | Great River Energy | N | N
A in MTEP21 |  | MRES | 20148 | 25856 | SwSta | 2026-07-31 | Appleton |  |  | 115 |  |  | Rebuild Appleton Substation from line breaker to a 4 position ring bus with 25 MVAR cap bank on the Appleton to Benson 115 kV line. | MN |  |  | Proposed | 5000000 | Planning | 2020 |  |  |  |  | Great River Energy | N | N
A in MTEP21 | West | MRES | 20445 | 26035 | CB | 2021-12-31 | J8 |  |  | 69 |  |  | Replace oil circuit breaker. | IA |  |  | Under Construction | 100000 | Budgetary | [5 empty] | Missouri River Energy Services (MRET) | N | N
A in MTEP21 | West | MRES | 20608 | 26075 | Dist | 2022-11-01 | New Worthington Substation |  |  | 69 |  |  | Distribution transformer to serve Worthington load. | MN |  |  | Proposed | 0 | Engineering Preliminary |  | Distribution costs of $3,400,000. Facility cost set to $0 as distribution cost should not be counted in MTEP. |  |  |  | Missouri River Energy Services (MRET) | N | N
A in MTEP21 | Central | NIPS | 20112 | 25818 | SUB | 2021-04-30 | Fair Oaks |  |  | 69 | 12 | 22.4 | Install new 138/69/12 switchable 22.4 MVA transformer. Install a new 69 kV line terminal with auto throwover scheme equipment for a new loop line to Colfax. Expand the fence and install new 69 kV rigid bus. | IN |  |  | Planned | 4700000 | Planning | [5 empty] | Wabash Valley Power Association, Inc. | N | N
A in MTEP21 | Central | NIPS | 20113 | 25819 | SUB | 2021-12-31 | Colfax South |  |  | 69 | 12 |  | Install a new 69 kV line terminal with an auto sectionalizing scheme equipment for a new loop line to Fair Oaks. | IN |  |  | Planned | 1500000 | Planning | [5 empty] | Wabash Valley Power Association, Inc. | N | N
A in MTEP21 | Central | NIPS | 20114 | 25820 | LN | 2021-12-31 | Fair Oaks | Colfax South | 1 | 69 | 12 | 68 | New 138kV (Operated at 69 kV) 477ACSR conductor looping Colfax to Fair Oaks for reliability in Jasper and Newton Counties. | IN |  | 5.3 | Planned | 5300000 | Planning |  |  | 68 |  |  | Wabash Valley Power Association, Inc. | N | N
A in MTEP21 | Central | NIPS | 20605 | 26048 | SwSta | 2022-12-31 | Shoreline Substation |  |  | 138 |  |  | New Switching Station. Shoreline will take the place of Michigan City Substation when it retires (2028) | IN |  |  | Planned | 16572178 | Scoping | [5 empty] | Northern Indiana Public Service Company | N | N
A in MTEP21 | West | OTP | 16286 | 24280 | LNup | 2020-12-15 | Donaldson 41.6 | Hallock 41.6 |  | 41.6 |  |  | Repole and reinsulate 8.8 miles to a 69 kV level on the transmission line between Donaldson-Hallock 41.6 kV line for reliability. | MN | 8.8 |  | M5_In Service | 1400483.7 | Actual |  | 4-15-2021 Costs updated from $1,383,590.00 to $1,400,483.70 Costs slightly over the original dollar amount due to weather delays. 1-15-2020 ISD changed from 3/31/2021 to 12/15/2020. Planning Status changed from Planning to In Service. Estimate Type changed from Planning to Actual. Costs updated from $1,300,000 to $1,383,590 7-15-2020 Tyler Jacobson - Project Engineer |  |  | The change in cost would be attributed to higher material costs and wintertime construction. | Otter Tail Power Company | N | N
A in MTEP21 | West | OTP | 19929 | 25613 | LNrb | 2021-12-01 | Finley 41.6 kV | McVille 41.6 kV | 1 | 41.6 |  |  | Rebuild 5.75 miles of 41.6 kV line and add automation to existing switches to improve reliability performance and restoration time of this line. | ND | 5.75 |  | Planned | 1000000 | Planning Preliminary |  | 4-13-2021 Updated 5 miles to 5.75 miles. 1-14-2021 Project Manager – Dennis Huffman Project Manager - Michael Riewer |  |  |  | Otter Tail Power Company | N | N
A in MTEP21 | West | OTP | 19930 | 25614 | LNrb | 2021-12-01 | Doyon 41.6 kV | Bartlett 41.6 kV |  | 41.6 |  |  | Rebuild 5.6 miles of 41.6 kV line, replace conductor and reroute existing line out of the water to improve reliability performance and restoration time of this line. | ND | 5.6 |  | Planned | 950000 | Planning Preliminary |  | 4-13-2021 Miles updated from 6 to 5.6 miles. Costs changed from $1M to $950,000. 1-14-2021 Project Manager – Dennis Huffman Project Manager - Michael Riewer |  |  |  | Otter Tail Power Company | N | N
A in MTEP21 | West | OTP | 20485 | 26038 | CAP | 2020-09-24 | Ortonville 115 kV |  |  | 115 |  |  | Reduce capacitor size from 30 MVAR to 17 MVAR. | MN |  |  | M5_In Service | 1000 | Actual |  | 1-15-2021 Toby reported costs update $5,000 to $1,000. Estimate Type changed to Actual. Project Leader - Aaron Demuth |  |  |  | Otter Tail Power Company | N | N
A in MTEP21 | West | OTP | 20606 | 26049 | TX | 2022-02-04 | Maple River 345/230/13.8 |  |  | 345 | 230 | 336 | Like-for-like replacement of the failed Maple River 345/230/13.8 kV transformer #1. Additionally, a new control house will be built. | ND |  |  | Planned | 2600000 | Planning Preliminary |  | Project Manager - Wayne P. 9/10/2021 ISD changed from 12/31/2021 to 2/4/2022. Reason for delay-Equipment delays has caused later construction and installation to install this transformer. 1/14/2021 ISD changed from 10/29/2022 to 12/31/2021. | 420 | Equipment delays has caused later construction and installation to install this transformer. |  | Otter Tail Power Company | N | N
A in MTEP21 | Central | PPI | 19847 | 25576 | SUB | 2024-12-31 | Golden |  | 1 | 138 | 69 | 84 | New 138/69 kV Golden substation near Golden, IL | IL |  |  | Planned | 6625000 | Budgetary | 2020 |  | 84 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 |  | PPI | 19847 | 25994 | LN | 2024-12-31 | Ameren Monument | Golden | 1 | 138 | 138 | 229 | New Ameren Monument - Golden 138 kV line in AEC | IL |  | 0.8 | Planned | 800000 | Budgetary | 2020 |  | 229 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19848 | 25577 | LN | 2024-12-31 | Camden | Rushville | 1 | 69 | 69 | 50 | New Camden - Rushville 69 kV line in AEC | IL |  | 12 | Planned | 7680000 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19849 | 25578 | LN | 2024-12-31 | Rushville | Sugar Grove | 1 | 69 | 69 | 50 | New Rushville - Sugar Grove 69 kV line in AEC | IL |  | 13 | Planned | 8448000 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19850 | 25579 | LN | 2024-12-31 | Sugar Grove | Mt. Sterling | 1 | 69 | 69 | 50 | New Sugar Grove - Mt. Sterling 69 kV line in AEC | IL |  | 9 | Planned | 5548800 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19851 | 25618 | LN | 2024-12-31 | Mt. Sterling | Kellerville | 1 | 69 |  | 69 | New Mt. Sterling - Kellerville 69 kV line in AEC | IL |  | 20.9 | Planned | 11328000 | Budgetary | 2020 |  | 69 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19932 | 25619 | LN | 2024-12-31 | Disco | Lomax | 1 | 69 | 69 | 50 | New Disco - Lomax 69 kV line in WIEC | IL |  | 15 | Planned | 9862500 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19933 | 25620 | LN | 2024-12-31 | Disco | Powellton | 1 | 69 | 69 | 50 | New Disco - Powellton 69 kV line in WIEC | IL |  | 12.5 | Planned | 8000000 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19934 | 25621 | CB | 2024-12-31 | Elvaston |  | 1 | 69 | 69 | 143 | Add breakers on the Elvaston - Powellton line and the Elvaston - Sutter line | IL |  |  | Planned | 350000 | Budgetary | 2020 |  | 143 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19935 | 25622 | LN | 2025-12-31 | Sutter | Ursa | 1 | 69 |  | 50 | New Sutter - Ursa 69 kV line between WIEC and AEC | IL |  | 21 | Planned | 13312000 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19937 | 25624 | SwSta | 2023-12-31 | Bluffs |  | 1 | 69 | 69 | 143 | New Bluffs 69 kV Breaker Station located near Bluffs, IL in IEC | IL |  |  | Planned | 2844450 | Budgetary | 2020 |  | 143 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19938 | 25625 | LNrb | 2020-12-31 | Grand Island | Poplar City | 1 | 69 | 69 | 69 | Rebuild Grand Island - Poplar City 69 kV Line in MEC | IL | 1.22 |  | M5_In Service | 557290 | Budgetary | 2020 |  | 69 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19939 | 25626 | LNrb | 2022-05-31 | Grand Island | Topeka | 1 | 69 | 69 | 69 | Rebuild Grand Island - Topeka 69 kV Line in MEC | IL | 5.27 |  | Planned | 2407310 | Budgetary | 2020 |  | 69 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19940 | 25627 | TX | 2024-12-31 | Grand Island |  | 1 | 138 | 69 | 84 | Replace Grand Island Delta-Wye 138/69 kV TX with Wye-Wye 138/69 kV TX | IL |  |  | Planned | 1500000 | Budgetary | 2020 |  | 84 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 |  | PPI | 19949 | 25928 | LN | 2025-12-31 | Crest | ISHI | 1 | 69 | 69 | 50 | New Crest - ISHI 69 kV line in SEC | IL |  | 3.15 | Planned | 2016000 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 |  | PPI | 19949 | 25927 | LN | 2025-12-31 | Johnston | Crest | 1 | 69 | 69 | 50 | New Johnston - Crest 69 kV line in SEC | IL |  | 0.2 | Planned | 128000 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 |  | PPI | 19949 | 25926 | LN | 2025-12-31 | Airport | Johnston | 1 | 69 | 69 | 50 | New Airport - Johnston 69 kV line in SEC | IL |  | 1.3 | Planned | 832000 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 |  | PPI | 19949 | 25920 | LN | 2025-12-31 | ISHI Dist | Airport | 1 | 69 | 69 | 50 | New ISHI Dist - Airport 69 kV line in SEC | IL |  | 1.7 | Planned | 1088000 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 19951 | 25634 | LNrb | 2023-12-31 | Pisgah | Berlin | 1 | 69 | 69 | 50 | Rebuild Pisgah Tap - Berlin 69 kV line between IEC and MEC | IL | 14.6 |  | Planned | 7880000 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 20607 | 26050 | CB | 2023-01-31 | Pittsfield |  | 1 | 69 |  | 143 | Interconnection Facilities: New 69 kV breaker at Pittsfield substation looking towards Panther Creek. | IL |  |  | Proposed | 281400 | Budgetary | 2020 |  | 143 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 20607 | 26054 | TEQ | 2023-01-31 | Pittsfield |  | 1 | 69 |  | 143 | Network Facilities: Upgrade Pittsfield substation to accommodate Panther Creek wind farm interconnection. | IL |  |  | Proposed | 1106500 | Budgetary | 2020 |  | 143 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 20607 | 26053 | LNrb | 2023-01-31 | Panther Creek | Pittsfield | 1 | 69 |  | 50 | Network Facilities: Upgrade Panther Creek to Pittsfield double circuit portion of El Dara to Pittsfield 69 kV line from 4/0 ACSR to 336.4 MCM ACSR | IL | 3.8 |  | Proposed | 3749733 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 20607 | 26052 | LN | 2023-01-31 | Panther Creek | Pittsfield | 1 | 69 |  | 50 | Interconnection Facilities: New 336.4 MCM ACSR interconnection transmission line. Double-circuited with Pittsfield - El Dara 69 kV line | IL |  | 3.8 | Proposed | 652968 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | Central | PPI | 20607 | 26051 | INT | 2023-01-31 | Panther Creek |  | 1 | 69 |  | 50 | Interconnection Facilities: New 69 kV substation facilities at Panther Creek substation | IL |  |  | Proposed | 885800 | Budgetary | 2020 |  | 50 |  |  | Prairie Power, Inc. | N | N
A in MTEP21 | South | SMEPA | 20305 | 25996 | INT | 2022-10-01 | MS Solar 4 |  |  | 161 |  |  | Construct a new 161kV breaker switching station that taps the Moselle - Columbia 161kV line for the POI for the Interconnection Customer project J1144. | MS |  |  | Planned | 5251585 | [6 empty] | South Mississippi Electric Power Association | N | N
A in MTEP21 | East | WPSC | 20885 | 26125 | TAP | 2022-12-31 | White Cloud | Wrights Creek | 1 | 69 |  |  | Install a Tap position for Consumer's Cimmaron Distribution Station | MI |  |  | Proposed | 600000 | Planning | 2022 |  |  |  |  | Wolverine Power Supply Cooperative, Inc. | N | N
A in MTEP21 | East | WPSC | 21205 | 26187 | LNrb | 2025-12-31 | Clinton Tap | Eaton Rapids |  | 138 |  |  | Rebuild line from Clinton Tap to Eaton Rapids | MI |  |  | Proposed | 8000000 | Planning | 2021 |  |  |  |  | Wolverine Power Supply Cooperative, Inc. | N | N
A in MTEP21 | East | WPSC | 21205 | 26194 | SUBmisc | 2025-12-31 | Clinton |  |  | 138 |  |  | Transformer Rotation | MI |  |  | Proposed | 1300000 | Planning | 2021 |  |  |  |  | Wolverine Power Supply Cooperative, Inc. | N | N
A in MTEP21 | East | WPSC | 21205 | 26193 | LNrc | 2025-12-31 | Clinton | Clinton Tap |  | 138 |  |  | Clinton to Clinton Tap reconductor | MI |  |  | Proposed | 2450000 | Planning | 2021 |  |  |  |  | Wolverine Power Supply Cooperative, Inc. | N | N
A in MTEP21 | East | WPSC | 21205 | 26192 | LNrb | 2025-12-31 | Clinton |  |  | 138 |  |  | Clinton Line Modifications | MI |  |  | Proposed | 1100000 | Planning | 2021 |  |  |  |  | Wolverine Power Supply Cooperative, Inc. | N | N
A in MTEP21 | East | WPSC | 21205 | 26191 | SUBmisc | 2025-12-31 | Otsego |  |  | 138 |  |  | Otsego 138kV BUS | MI |  |  | Proposed | 200000 | Planning | 2021 |  |  |  |  | Wolverine Power Supply Cooperative, Inc. | N | N
A in MTEP21 | East | WPSC | 21205 | 26190 | SUBmisc | 2025-12-31 | Hastings |  |  | 138 |  |  | Hastings 139kV BUS | MI |  |  | Proposed | 200000 | Planning | 2021 |  |  |  |  | Wolverine Power Supply Cooperative, Inc. | N | N
A in MTEP21 | East | WPSC | 21205 | 26189 | SUBmisc | 2025-12-31 | Vermontville |  |  | 138 |  |  | 138kV BUS at Vermontville | MI |  |  | Proposed | 200000 | Planning | 2021 |  |  |  |  | Wolverine Power Supply Cooperative, Inc. | N | N
A in MTEP21 | East | WPSC | 21205 | 26188 | SUBmisc | 2025-12-31 | Eaton Rapids |  |  | 138 |  |  | Eaton Rapids 128kV BUS | MI |  |  | Proposed | 200000 | Planning | [5 empty] | Wolverine Power Supply Cooperative, Inc. | N | N
A in MTEP21 | West | XEL | 19165 | 25413 | SUB | 2022-07-01 | Fieldon |  |  | 345 |  |  | Removes the existing Fieldon substation and series capacitor. | MN |  |  | Proposed | 2900000 | Planning | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 |  | XEL | 19165 | 25414 | LNup | 2022-07-01 | Wilmarth | Crandall |  | 345 |  |  | Bypasses and retires Fieldon series capacitor and substation connecting Wilmarth directly to Crandall. | MN |  |  | Proposed | 100000 | Planning | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19886 | 25583 | TX | 2021-12-15 | MN Valley |  |  | 115 | 69 |  | Like for like replacement of Minnesota Valley TR12. TR12 is 68 years old and is experiencing performance issues. | MN |  |  | Planned | 1500000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19887 | 25584 | TX | 2021-12-15 | Eau Claire |  |  | 345 | 161 |  | End of life, like for like replacement of Eau Claire TR10. Experiencing performance issues. | WI |  |  | Planned | 3000000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19888 | 25585 | LNrb | 2022-12-15 | Northfield | Farmington | 1 | 69 |  |  | End of life rebuild approximately 18.6 miles of existing line to current Transmission Design Standards. Reconductor 1.3 miles | MN | 18.6 |  | Proposed | 8000000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19889 | 25586 | LNrb | 2024-06-01 | Black Oak | Sauk Center | 1 | 69 |  |  | Rebuild and upgrade conductor on approximately 6.64 miles. | MN |  |  | Proposed | 4000000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19890 | 25587 | LNrb | 2022-12-15 | Watkins | Kimball |  | 69 |  |  | Rebuild and upgrade approximately 6.56 miles of existing line. Replace EOL switches and MODs. | MN |  |  | Proposed | 3200000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19891 | 25588 | SUB | 2021-03-15 | Green Isle |  |  | 69 | 13.8 |  | New 69/12.8kV Substation 7MVA 69/13.8kV Transformer Single 69kV line in and out from line between Arlington and Carver County 69kV | MN |  |  | Planned | 3500000 | Planning Preliminary |  | Distribution Project $2.7M Distribution cost $0.8M Transmission cost |  |  |  | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19892 | 25589 | TX | 2021-12-15 | Elm Creek |  |  | 115 | 34.5 |  | Install Elm Creek TR4 at 115kV/34.5kV with one new 34.5kV feeders exiting the substation to remediate N-1 overloads and allow proposed new customer load | MN |  |  | Planned | 4070000 | Planning Preliminary |  | Distribution Project $0.92M Transmission $3.15M Distribution |  |  |  | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19893 | 25590 | SUB | 2022-10-15 | Great Plains |  |  | 115 | 13.8 |  | Construct new 115kV substation in Sioux Falls, SD between West Sioux Falls - Cherry Creek 115kV; 4 rows breaker-and-a-half; 3 TRs, 4 lines, 115 kV cap. | SD |  |  | Planned | 10600000 | Planning Preliminary |  | Distribution Project $7.6M Distribution $3.0M Transmission |  |  |  | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19905 | 25591 | TAP | 2021-04-14 | Inver Grove | Keagan Lake Tap | 1 | 69 |  |  | Install 3-way switch on 69kV line between Inver Grove - Keagan Lake Tap to accommodate GRE’s new Barnes Grove interconnection | MN |  |  | Planned | 350000 | Planning Preliminary |  | Line tap and switch to accommodate GRE Interconnection MTEP 2589 |  |  |  | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19906 | 25592 | CAP | 2021-12-15 | Prentice |  |  | 115 |  |  | Upgrade the cap bank to 10MVAR and replace the circuit switcher at Prentice substation. | WI |  |  | Planned | 1000000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19913 | 25601 | LNrb | 2024-06-15 | Howard Lake | Big Swan | 1 | 69 |  |  | Howard Lake to Big Swan - Rebuild 16.0 miles to current 69kV standard for end of life asset renewal | MN | 16 |  | Planned | 8960000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 |  | XEL | 19913 | 25603 | LNrb | 2024-06-15 | Cokato | Winstead |  | 69 |  |  | Cokato to Winstead – Rebuild 14.3 miles to current 69kV standard for end of life asset renewal | MN | 14.3 |  | Planned | 8008000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 |  | XEL | 19913 | 25602 | LNrb | 2024-06-15 | Delano | Howard Lake | 1 | 69 |  |  | Delano to Howard Lake – Rebuild 19.7 miles to current 69kV standard for end of life asset renewal | MN | 19.7 |  | Planned | 11032000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19914 | 25604 | LNrb | 2023-05-01 | High Bridge | Rogers Lake | 1 | 115 |  |  | Convert the bifurcated 115 kV line from High Bridge to Rogers Lake to a double circuit 115 kV line to alleviate curtailment on the High Bridge Generating Plant. Construct new breaker positions at High Bridge and Rogers Lake tol accommodate the second 115kV circuit | MN |  |  | Planned | 3420000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19915 | 25605 | SUB | 2022-10-15 | Alma |  |  | 69 | 12.5 |  | Replace the existing Alma sub which is at end of life and in a poor access location with new sub with 7MVA TR with two regulated feeders at new site. | WI |  |  | Planned | 3000000 | Planning Preliminary |  | Distribution Project Distribution $2.7M Transmission: $300k |  |  |  | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 19916 | 25606 | SUB | 2022-10-15 | Genoa |  |  | 69 | 13.8 |  | Rebuild Genoa sub which is at end of life with New sub with 7MVA TR with two feeders on the existing site. | WI |  |  | Planned | 2700000 | Planning Preliminary |  | Distribution project Distribution $2.4M Transmission: $300k |  |  |  | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 20135 | 25841 | SwSta | 2024-12-31 | Adams Wind Tap |  |  | 69 |  |  | Convert Adams Wind Tap to a breaker station with 2 breakers and 1 MOD | MN |  |  | Planned | 2700000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 |  | XEL | 20135 | 25845 | LNrb | 2024-12-31 | Panther | Big Swan | 1 | 69 |  |  | Rebuild Line to 477ACSR for age and condition and to support Adams wind upgrade | MN |  |  | Planned | 30600000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
A in MTEP21 | West | XEL | 20229 | 25982 | TX | 2023-11-10 | Stone Lake |  |  | 345 | 161 |  | Transformer upgrade for J732 in Aug 17 ATC DPP cycle | WI |  |  | Planned | 3600000 | Planning Preliminary | [5 empty] | Northern States Power (Xcel Energy) | N | N
Note on P1: Upgraded or on existing rights of way